## Calculator
Water Pipe Size Calculator
Types of Pipe | Select | Cast Iron (CI)
C-Value of Pipe | Auto | 100 |  | Available pipe sizes to select from
Flowrate | usgpm | 2150 |  | Pipe size (inch) | Pipe Size (MM)
Maximum Allowable Frictional Loss | ft/100ft | 4 |  | 0.5 | 12.7
Min. Required Pipe Internal Diameter | inch | 10.0767 |  | 0.75 | 19.05
|  |  |  | 1 | 25.4
% tolerance to the imposed allowable friction loss* | % | 0 |  | 1.25 | 31.75
Selected pipe size** | inch | 12 |  | 1.5 | 38.1
|  |  |  | 2 | 50.8
|  |  |  | 2.5 | 63.5
Remarks |  |  |  | 3 | 76.2
*Sometimes we want to retain the pipe size at one size smaller if |  | 4 | ft/100ft | 3.5 | 88.9
is only exceeded by a little |  |  |  | 4 | 101.6
0% means no tolerance - Upsize once it is exceeded |  |  |  | 5 | 127
100% means to up one size no matter what |  |  |  | 6 | 152.4
**Macro-enabled function, hold down 'CTRL' & 'SHIFT' & press 'ENTER' in the formula bar if prompted "N/A" error |  |  |  | 8 | 203.2
Highlighted Green is data to input, including the list of available pipe sizes on the right |  |  |  | 10 | 254
|  |  |  | 12 | 304.8
|  |  |  | 14 | 355.6
|  |  |  | 16 | 406.4
|  |  |  | 18 | 457.2
|  |  |  | 20 | 508
|  |  |  | 22 | 558.8
|  |  |  | 24 | 609.6
|  |  |  | 26 | 660.4
|  |  |  | 28 | 711.2
|  |  |  | 30 | 762
|  |  |  | 32 | 812.8
|  |  |  | 34 | 863.6
|  |  |  | 36 | 914.4
|  |  |  | 38 | 965.2
|  |  |  | 40 | 1016
|  |  |  | 42 | 1066.8
|  |  |  | 44 | 1117.6
|  |  |  | 46 | 1168.4
|  |  |  | 48 | 1219.2
|  |  |  | 50 | 1270
|  |  |  | 52 | 1320.8
|  |  |  | 54 | 1371.6
|  |  |  | 56 | 1422.4
|  |  |  | 58 | 1473.2
|  |  |  | 60 | 1524
|  |  |  | 62 | 1574.8
|  |  |  | 64 | 1625.6
|  |  |  | 66 | 1676.4
|  |  |  | 68 | 1727.2
|  |  |  | 70 | 1778
|  |  |  | 72 | 1828.8
|  |  |  | 74 | 1879.6

## C-Value Reference
TYPE OF PIPE | C value
General Metal (Extremely smooth) | 130
Cast Iron (CI) | 100
Cast Iron Cement Lined (CICL) | 130
Cast Iron Bituminous Lined (CIBL) | 130
Cast Iron (Asphalt Coated) | 100
Ductile Iron (DI) | 110
Ductile Iron Cement Lined (DICL) | 130
Mild Steel (MS) | 120
Mild Steel Cement Lined (MSCL) | 130
Galvanised Iron (GI) | 120
Stainless steel | 140
Steel | 100
Steel (Corrugated) | 60
Copper (Cu) | 140
Aluminium (Al) | 130
Brass (Br) | 130
Lead | 130
Tin | 130
Corrugated metal | 60
Reinforced glass fibre (FRP) | 140
Plastic (General) | 130
High-density polyethylene (HDPE) | 150
Acrylonite Butadiene Styrene (ABS) | 130
Polyethylene (PE) | 140
Polyvinyl chloride (PVC, CPVC) | 150
Spun Cement | 130
Concrete | 100
Vitrified clay | 110
Wooden | 110
Masonry | 110
Glass | 130