## Backcode Size
Medical Gas Pressure Drop Calculator (Suggested Pipe Size)
Pipeline Pressure (bar) | Vacuum
Measured Length of Pipe (m) | 122
Pipe Size, Outer Diameter (mm)
Design Flow (LPM) | 120
Match Nearest Pipe Length (m) | 122
Column | 6
Hard Code Address | H
Hard Code Address 2 | H5:H40
Row | 17
Row With Error Message | 17
Match Nearest Flow | 130
Match Nearest Flow (LPM) | 130
Pressure Drop from Table | 1.3
Match Pressure Drop from Table (kPa) | 1.3
Pressure Drop (kPa) | 1.1077
Computed Pressure Drop (kPa) | 1.1077
Pressure Drop + 30% Fitting Loss | 1.44
Pressure Drop + 30% Fitting Loss (kPa) | 1.44
Suggested Pipe Size | 35
% PD | 2.4407
% PD | 2.4407
* Suggested pipe size shall be subject to acceptable pressure drop %. To observe the effect of change of pipe
size on the pressure drop, use the next calculator

## Enter size
Medical Gas Pressure Drop Calculator (Manual Enter Size)
Pipeline Pressure (bar) | Vacuum
Measured Length of Pipe (m) | 405
Pipe Size, Outer Diameter (mm) | 76
Design Flow (LPM) | 2350
Match Nearest Pipe Length (m) | 396
Column | 15
Hard Code Address | Q
Hard Code Address 2 | Q33:Q36
Pipe Size Row Lookup Min | 33
Pipe Size Row Lookup Max | 36
Row | 36
Row With Error Message | 36
Row (with Reference to Start Row C5) | 32
Row With Error Message | 32
Match Nearest Flow | 1547
Match Nearest Flow (LPM) | 1547
Pressure Drop from Table | 6.5
Match Pressure Drop from Table (kPa) | 6.5
Pressure Drop (kPa) | 15.3401
Computed Pressure Drop (kPa) | 15.3401
Pressure Drop + 30% Fitting Loss | 19.9421
Pressure Drop + 30% Fitting Loss | 19.9421
% PD | 33.8002
% PD | 33.8002

## 4 bar (hidden)
British Standard Size Tube BS EN 1057:R250, Table X |  | Distance from Source (m) at 4 bar for 7, 14, 21kPa Pressure Loss
Outside Diameter (mm) | Pressure Loss (kPa) | 8 | 15 | 30 | 61 | 91 | 122 | 152 | 183 | 213 | 244 | 274 | 305 | 335 | 366 | 396 | 427 | 457
Free air flow rate (L/min)
12 | 7 | 311 | 209 | 141 | 95 | 75 | 64 | 56 | 50 | 46 | 43 | 40 | 37 | 35 | 34 | 32 | 31 | 30
12 | 14 | 455 | 307 | 207 | 139 | 110 | 94 | 82 | 74 | 68 | 63 | 59 | 55 | 52 | 50 | 47 | 45 | 44
12 | 21 | 564 | 382 | 258 | 174 | 138 | 117 | 103 | 93 | 85 | 78 | 73 | 69 | 65 | 62 | 59 | 57 | 55
|  | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100
15 | 7 | 579 | 391 | 263 | 177 | 140 | 119 | 105 | 94 | 86 | 80 | 75 | 70 | 66 | 63 | 60 | 58 | 56
15 | 14 | 845 | 572 | 386 | 260 | 207 | 175 | 154 | 139 | 127 | 118 | 110 | 104 | 98 | 93 | 89 | 85 | 82
15 | 21 | 1038 | 711 | 481 | 325 | 258 | 219 | 192 | 173 | 159 | 147 | 137 | 129 | 122 | 117 | 111 | 107 | 102
|  | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100
22 | 7 | 1677 | 1135 | 768 | 518 | 411 | 349 | 307 | 277 | 254 | 235 | 220 | 207 | 196 | 186 | 178 | 170 | 164
22 | 14 | 2441 | 1656 | 1123 | 759 | 604 | 513 | 451 | 407 | 373 | 345 | 323 | 304 | 288 | 274 | 262 | 251 | 241
22 | 21 | 3023 | 2053 | 1395 | 945 | 751 | 638 | 562 | 507 | 465 | 431 | 403 | 379 | 359 | 342 | 326 | 313 | 301
|  | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100
28 | 7 | 3363 | 2283 | 1547 | 1047 | 832 | 706 | 622 | 560 | 514 | 476 | 445 | 419 | 397 | 378 | 361 | 346 | 332
28 | 14 | 4881 | 3320 | 2257 | 1530 | 1218 | 1035 | 912 | 823 | 754 | 699 | 653 | 615 | 583 | 555 | 530 | 508 | 488
28 | 21 | 6034 | 4109 | 2800 | 1901 | 1514 | 1287 | 1135 | 1024 | 938 | 870 | 814 | 767 | 726 | 691 | 660 | 633 | 609
|  | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100
35 | 7 | 6023 | 4096 | 2783 | 1886 | 1500 | 1275 | 1124 | 1013 | 928 | 861 | 805 | 758 | 718 | 683 | 653 | 626 | 602
35 | 14 | 8720 | 5943 | 4051 | 2752 | 2192 | 1865 | 1644 | 1483 | 1360 | 1261 | 1180 | 1111 | 1053 | 1002 | 957 | 918 | 883
35 | 21 | 10758 | 7344 | 5018 | 3415 | 2723 | 2317 | 2044 | 1845 | 1692 | 1569 | 1468 | 1383 | 1310 | 1248 | 1192 | 1143 | 1099
|  | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100
42 | 7 | 10103 | 6883 | 4685 | 3180 | 2533 | 2154 | 1899 | 1713 | 1570 | 1456 | 1362 | 1283 | 1215 | 1157 | 1105 | 1060 | 1019
42 | 14 | 14587 | 9963 | 6806 | 4633 | 3694 | 3145 | 2775 | 2504 | 2296 | 2130 | 1993 | 1878 | 1780 | 1694 | 1619 | 1553 | 1493
42 | 21 | 17963 | 12290 | 8421 | 5743 | 4584 | 3904 | 3446 | 3112 | 2855 | 2648 | 2478 | 2335 | 2213 | 2107 | 2014 | 1932 | 1858
|  | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100
54 | 7 | 14974 | 10588 | 7487 | 5294 | 4323 | 3743 | 3348 | 3056 | 2830 | 2647 | 2496 | 2368 | 2257 | 2161 | 2076 | 2001 | 1933
54 | 14 | 21176 | 14974 | 10588 | 7487 | 6113 | 5294 | 4735 | 4323 | 4002 | 3743 | 3529 | 3348 | 3192 | 3056 | 2937 | 2830 | 2734
54 | 21 | 25935 | 18339 | 12968 | 9169 | 7487 | 6484 | 5799 | 5294 | 4901 | 4585 | 4323 | 4101 | 3910 | 3743 | 3597 | 3466 | 3348
|  | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100
76 | 7 | 37754 | 26696 | 18877 | 13348 | 10899 | 9438 | 8442 | 7706 | 7135 | 6674 | 6292 | 5969 | 5692 | 5449 | 5236 | 5045 | 4874
76 | 14 | 53392 | 37754 | 26696 | 18877 | 15413 | 13348 | 11939 | 10899 | 10090 | 9438 | 8899 | 8442 | 8049 | 7706 | 7404 | 7135 | 6893
76 | 21 | 65392 | 46239 | 32696 | 23119 | 18877 | 16348 | 14622 | 13348 | 12358 | 11560 | 10899 | 10339 | 9858 | 9438 | 9068 | 8738 | 8442
|  | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100
1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100
1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100
1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100
1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100
######## To ignore

## 7 bar (hidden)
British Standard Size Tube BS EN 1057:R250, Table X |  | Distance from Source (m) at 7 bar for 7, 14, 34 kPa Pressure Loss
Outside Diameter (mm) | Pressure Loss (kPa) | 8 | 15 | 30 | 61 | 91 | 122 | 152 | 183 | 213 | 244 | 274 | 305 | 335 | 366 | 396 | 427 | 457
Free air flow rate (L/min)
12 | 7 | 408 | 276 | 186 | 125 | 99 | 84 | 74 | 67 | 61 | 56 | 53 | 50 | 47 | 45 | 43 | 41 | 39
12 | 14 | 599 | 405 | 274 | 185 | 147 | 124 | 109 | 99 | 90 | 84 | 78 | 74 | 70 | 66 | 63 | 61 | 58
12 | 34 | 979 | 664 | 450 | 304 | 242 | 205 | 181 | 163 | 149 | 138 | 129 | 122 | 115 | 110 | 105 | 100 | 96
|  | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100
15 | 7 | 759 | 514 | 347 | 234 | 186 | 158 | 139 | 125 | 114 | 106 | 99 | 93 | 88 | 84 | 80 | 77 | 74
15 | 14 | 1112 | 754 | 510 | 345 | 274 | 232 | 205 | 184 | 169 | 156 | 146 | 138 | 130 | 124 | 118 | 114 | 109
15 | 34 | 1811 | 1231 | 836 | 566 | 450 | 383 | 337 | 304 | 279 | 258 | 242 | 227 | 215 | 205 | 196 | 188 | 180
|  | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100
22 | 7 | 2192 | 1488 | 1009 | 682 | 542 | 460 | 406 | 366 | 335 | 310 | 290 | 273 | 259 | 246 | 235 | 225 | 217
22 | 14 | 3198 | 2175 | 1478 | 1001 | 797 | 677 | 597 | 538 | 493 | 457 | 428 | 403 | 381 | 363 | 347 | 332 | 320
22 | 34 | 5180 | 3533 | 2410 | 1638 | 1306 | 1111 | 980 | 884 | 811 | 752 | 704 | 663 | 628 | 598 | 571 | 548 | 527
|  | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100
28 | 7 | 4387 | 2984 | 2027 | 1374 | 1093 | 929 | 819 | 739 | 677 | 628 | 587 | 553 | 524 | 498 | 476 | 456 | 439
28 | 14 | 6382 | 4351 | 2963 | 2013 | 1604 | 1364 | 1203 | 1086 | 995 | 923 | 863 | 813 | 771 | 734 | 701 | 672 | 646
28 | 34 | 10290 | 7038 | 4816 | 3283 | 2620 | 2232 | 1970 | 1779 | 1632 | 1514 | 1417 | 1335 | 1266 | 1205 | 1152 | 1105 | 1063
|  | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100
35 | 7 | 7841 | 5345 | 3638 | 2470 | 1968 | 1674 | 1476 | 1332 | 1221 | 1132 | 1059 | 998 | 945 | 900 | 860 | 825 | 793
35 | 14 | 11380 | 7775 | 5307 | 3612 | 2881 | 2453 | 2165 | 1954 | 1792 | 1662 | 1556 | 1466 | 1389 | 1323 | 1264 | 1212 | 1166
35 | 34 | 18271 | 12528 | 8599 | 5876 | 4696 | 4003 | 3536 | 3194 | 2931 | 2720 | 2547 | 2401 | 2276 | 2168 | 2073 | 1988 | 1912
|  | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100
42 | 7 | 13128 | 8964 | 6113 | 4159 | 3316 | 2823 | 2490 | 2248 | 2061 | 1912 | 1789 | 1686 | 1598 | 1521 | 1454 | 1394 | 1341
42 | 14 | 19010 | 13012 | 8901 | 6070 | 4847 | 4129 | 3646 | 3293 | 3021 | 2803 | 2624 | 2473 | 2344 | 2232 | 2134 | 2047 | 1969
42 | 34 | 30392 | 20892 | 14381 | 9849 | 7881 | 6723 | 5942 | 5371 | 4930 | 4577 | 4286 | 4042 | 3833 | 3651 | 3491 | 3349 | 3223
|  | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100
1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100
1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100
1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100
1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100
1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100
1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100
1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100
1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100
1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100
1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100
1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100
1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100
######## To ignore

## 11 bar (hidden)
British Standard Size Tube BS EN 1057:R250, Table X |  | Distance from Source (m) at 11 bar for 7, 14, 34 kPa Pressure Loss
Outside Diameter (mm) | Pressure Loss (kPa) | 8 | 15 | 30 | 61 | 91 | 122 | 152 | 183 | 213 | 244 | 274 | 305 | 335 | 366 | 396 | 427 | 457
Free air flow rate (L/min)
12 | 7 | 487 | 356 | 252 | 177 | 144 | 124 | 112 | 102 | 94 | 88 | 84 | 79 | 75 | 72 | 69 | 67 | 65
12 | 14 | 689 | 503 | 355 | 249 | 204 | 177 | 158 | 144 | 133 | 124 | 118 | 111 | 106 | 102 | 98 | 94 | 91
12 | 34 | 1084 | 791 | 560 | 392 | 321 | 277 | 249 | 227 | 210 | 197 | 185 | 176 | 167 | 161 | 154 | 148 | 143
|  | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100
15 | 7 | 867 | 634 | 448 | 314 | 257 | 222 | 199 | 181 | 168 | 157 | 148 | 141 | 134 | 128 | 124 | 119 | 115
15 | 14 | 1226 | 895 | 633 | 444 | 363 | 314 | 281 | 257 | 238 | 222 | 209 | 199 | 189 | 181 | 174 | 168 | 162
15 | 34 | 1929 | 1409 | 996 | 698 | 572 | 494 | 443 | 403 | 373 | 350 | 330 | 313 | 298 | 285 | 275 | 264 | 256
|  | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100
22 | 7 | 2332 | 1703 | 1205 | 845 | 692 | 598 | 535 | 487 | 452 | 423 | 399 | 378 | 360 | 345 | 332 | 319 | 309
22 | 14 | 3294 | 2405 | 1701 | 1193 | 977 | 844 | 755 | 689 | 638 | 597 | 562 | 534 | 509 | 487 | 468 | 451 | 436
22 | 34 | 5185 | 3787 | 2678 | 1878 | 1537 | 1328 | 1189 | 1084 | 1005 | 939 | 886 | 840 | 801 | 767 | 737 | 710 | 686
|  | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100
28 | 7 | 4469 | 3263 | 2308 | 1618 | 1325 | 1145 | 1025 | 935 | 866 | 809 | 764 | 724 | 691 | 660 | 636 | 612 | 591
28 | 14 | 6311 | 4608 | 3259 | 2286 | 1872 | 1616 | 1448 | 1320 | 1223 | 1143 | 1078 | 1022 | 976 | 933 | 897 | 864 | 835
28 | 34 | 9935 | 7255 | 5130 | 3598 | 2946 | 2544 | 2279 | 2077 | 1926 | 1799 | 1698 | 1609 | 1535 | 1469 | 1412 | 1359 | 1315
|  | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100
35 | 7 | 7718 | 5636 | 3985 | 2795 | 2289 | 1976 | 1771 | 1614 | 1495 | 1397 | 1319 | 1250 | 1192 | 1141 | 1097 | 1056 | 1021
35 | 14 | 10898 | 7959 | 5628 | 3947 | 3231 | 2791 | 2500 | 2279 | 2112 | 1973 | 1862 | 1765 | 1684 | 1611 | 1549 | 1492 | 1442
35 | 34 | 17157 | 12530 | 8860 | 6213 | 5087 | 4394 | 3936 | 3587 | 3325 | 3107 | 2932 | 2779 | 2651 | 2537 | 2439 | 2348 | 2271
|  | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100
42 | 7 | 12550 | 9166 | 6481 | 4545 | 3721 | 3214 | 2879 | 2624 | 2432 | 2272 | 2144 | 2033 | 1940 | 1855 | 1784 | 1718 | 1661
42 | 14 | 17724 | 12944 | 9152 | 6418 | 5255 | 4538 | 4066 | 3706 | 3435 | 3209 | 3029 | 2871 | 2739 | 2620 | 2519 | 2426 | 2345
42 | 34 | 27902 | 20377 | 14409 | 10104 | 8273 | 7145 | 6401 | 5834 | 5407 | 5052 | 4768 | 4519 | 4312 | 4125 | 3966 | 3819 | 3692
|  | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100
1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100
1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100
1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100
1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100
1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100
1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100
1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100
1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100
1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100
1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100
1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100
1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100
######## To ignore

## Vacuum (hidden)
British Standard Size Tube BS EN 1057: R250, Table X |  | Distance from source (m) at 59 kPa (450 mm Hg) for 1.3, 2.6, 3.9, 6.5 kPa (10, 20, 30, 50 mm Hg) pressure loss
Outside Diameter (mm) | Pressure Loss (kPa) | 8 | 15 | 30 | 61 | 91 | 122 | 152 | 183 | 213 | 244 | 274 | 305 | 335 | 366 | 396 | 427 | 457
Free air flow rate (L/min)
12 | 1.3 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100
12 | 2.6 | 47 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100
12 | 3.9 | 60 | 40 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100
12 | 6.5 | 82 | 55 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100
15 | 1.3 | 59 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100
15 | 2.6 | 89 | 59 | 40 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100
15 | 3.9 | 113 | 76 | 51 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100
15 | 6.5 | 153 | 103 | 69 | 46 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100
22 | 1.3 | 173 | 116 | 78 | 52 | 41 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100
22 | 2.6 | 260 | 174 | 117 | 79 | 62 | 53 | 46 | 42 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100
22 | 3.9 | 330 | 222 | 149 | 100 | 79 | 67 | 59 | 53 | 49 | 45 | 42 | 40 | 1e+100 | 1e+100 | 1e+100 | 1e+100 | 1e+100
22 | 6.5 | 445 | 301 | 203 | 137 | 108 | 92 | 81 | 73 | 67 | 62 | 57 | 54 | 51 | 49 | 46 | 45 | 43
28 | 1.3 | 350 | 236 | 159 | 106 | 84 | 71 | 63 | 56 | 51 | 48 | 44 | 42 | 40 | 1e+100 | 1e+100 | 1e+100 | 1e+100
28 | 2.6 | 525 | 353 | 238 | 160 | 127 | 107 | 94 | 85 | 78 | 72 | 67 | 63 | 60 | 57 | 54 | 52 | 50
28 | 3.9 | 666 | 448 | 303 | 204 | 161 | 137 | 120 | 108 | 99 | 92 | 86 | 81 | 76 | 73 | 69 | 66 | 64
28 | 6.5 | 900 | 607 | 412 | 278 | 220 | 187 | 164 | 148 | 135 | 125 | 117 | 110 | 104 | 99 | 95 | 91 | 87
35 | 1.3 | 637 | 427 | 288 | 193 | 153 | 130 | 114 | 102 | 94 | 87 | 81 | 76 | 72 | 69 | 65 | 63 | 60
35 | 2.6 | 947 | 638 | 431 | 290 | 230 | 195 | 171 | 154 | 141 | 131 | 122 | 115 | 109 | 103 | 99 | 95 | 91
35 | 3.9 | 1198 | 808 | 548 | 369 | 293 | 248 | 218 | 197 | 180 | 167 | 156 | 147 | 139 | 132 | 126 | 121 | 116
35 | 6.5 | 1614 | 1091 | 743 | 503 | 399 | 339 | 298 | 269 | 246 | 228 | 213 | 200 | 190 | 180 | 172 | 165 | 158
42 | 1.3 | 1074 | 724 | 488 | 328 | 260 | 220 | 194 | 174 | 160 | 148 | 138 | 130 | 123 | 117 | 111 | 107 | 103
42 | 2.6 | 1598 | 1079 | 731 | 493 | 391 | 331 | 291 | 262 | 240 | 222 | 208 | 196 | 185 | 176 | 168 | 161 | 155
42 | 3.9 | 2016 | 1363 | 926 | 626 | 497 | 422 | 371 | 334 | 306 | 283 | 265 | 249 | 236 | 224 | 214 | 205 | 197
42 | 6.5 | 2706 | 1833 | 1254 | 851 | 677 | 574 | 506 | 456 | 417 | 387 | 361 | 340 | 322 | 306 | 293 | 280 | 270
54 | 1.3 | 2191 | 1480 | 1001 | 674 | 535 | 453 | 399 | 359 | 329 | 304 | 284 | 268 | 253 | 241 | 230 | 220 | 212
54 | 2.6 | 3246 | 2196 | 1493 | 1010 | 802 | 681 | 599 | 540 | 494 | 458 | 428 | 403 | 381 | 363 | 346 | 332 | 319
54 | 3.9 | 4083 | 2766 | 1889 | 1281 | 1019 | 865 | 762 | 687 | 629 | 582 | 545 | 513 | 485 | 462 | 441 | 423 | 406
54 | 6.5 | 5448 | 3699 | 2549 | 1737 | 1384 | 1176 | 1037 | 935 | 856 | 794 | 742 | 699 | 662 | 630 | 601 | 576 | 554
76 | 1.3 | 5521 | 3773 | 2563 | 1733 | 1377 | 1169 | 1029 | 927 | 849 | 786 | 735 | 692 | 655 | 623 | 595 | 570 | 548
76 | 2.6 | 8070 | 5563 | 3807 | 2586 | 2058 | 1749 | 1541 | 1389 | 1273 | 1179 | 1103 | 1038 | 983 | 936 | 894 | 857 | 823
76 | 3.9 | 10041 | 6968 | 4801 | 3274 | 2609 | 2219 | 1957 | 1765 | 1617 | 1499 | 1402 | 1320 | 1250 | 1190 | 1137 | 1090 | 1048
76 | 6.5 | 13166 | 9233 | 6439 | 4421 | 3533 | 3009 | 2655 | 2396 | 2197 | 2037 | 1906 | 1796 | 1701 | 1619 | 1547 | 1483 | 1426
108 | 1.3 | 12874 | 9140 | 6543 | 4552 | 3732 | 3280 | 2879 | 2628 | 2433 | 2276 | 1919 | 2036 | 1941 | 1858 | 1785 | 1712 | 1641
108 | 2.6 | 18207 | 12874 | 9235 | 6578 | 5274 | 4552 | 4071 | 3716 | 3441 | 3219 | 3035 | 2879 | 2745 | 2628 | 2525 | 2422 | 2325
108 | 3.9 | 22494 | 15905 | 11374 | 8114 | 6509 | 5657 | 5030 | 4592 | 4251 | 3976 | 3750 | 3557 | 3391 | 3247 | 3119 | 2992 | 2870
108 | 6.5 | 29238 | 20675 | 14708 | 10520 | 8445 | 7343 | 6538 | 5968 | 5526 | 5169 | 4873 | 4623 | 4408 | 4220 | 4055 | 3889 | 3730
######## To ignore

## Reference (hidden)
Matched Row | Row Address |  | Pipe Size | Row Start | Row End | Row Difference | Pressure | Pressure (kPa)
1 | C |  | 12 | 5 | 8 | 4 | 4 bar | 400
2 | D |  | 15 | 9 | 12 | 8 | 7 bar | 700
3 | E |  | 22 | 13 | 16 | 12 | 11 bar | 1100
4 | F |  | 28 | 17 | 20 | 16 | Vacuum | 59
5 | G |  | 35 | 21 | 24 | 20
6 | H |  | 42 | 25 | 28 | 24
7 | I |  | 54 | 29 | 32 | 28
8 | J |  | 76 | 33 | 36 | 32
9 | K |  | 108 | 37 | 40 | 36
10 | L
11 | M
12 | N
13 | O
14 | P
15 | Q
16 | R
17 | S
Examples
Example | Pressure | Length of Pipe | Pipe size | Design Flow
1 | 4 bar | 52 m | 22 mm | 150 LPM
2 | 4 bar | 52 m | 28 mm | 150 LPM
3 | 4 bar | 52 m | 42 mm | 150 LPM
4 | 4 bar | 52 m | 54 mm | 150 LPM
Example | Pressure | Length of Pipe | Pipe size | Design Flow
1 | 7 bar | 52 m | 28 mm | 150 LPM
2 | 7 bar | 52 m | 28 mm | 1050 LPM
3 | 7 bar | 52 m | 28 mm | 2350 LPM
4 | 7 bar | 52 m | 28 mm | 8000 LPM
Example | Pressure | Length of Pipe | Pipe size | Design Flow
1 | 11 bar | 52 m | 28 mm | 150 LPM
2 | 11 bar | 252 m | 28 mm | 150 LPM
3 | 11 bar | 405 m | 28 mm | 150 LPM
4 | 11 bar | 1000 m | 28 mm | 150 LPM
Example | Pressure | Length of Pipe | Pipe size | Design Flow
1 | 11 bar | 52 m | 22 mm | 150 LPM
2 | 11 bar | 252 m | 54 mm | 1050 LPM
3 | 11 bar | 405 m | 76 mm | 2350 LPM
4 | 11 bar | 1000 m | 108 mm | 8000 LPM