## Calc
Duct Sizer & Duct Loss Calculator
Key:
Parameters | Symbol | Units | Values |  | *[User input Data]
Airflow | Q | cfm | 1000
Duct Material | - | - | Galvanised Iron
Absolute Roughness | ε | mm | 0.15
Pressure Drop per unit length | ΔP/L | "w.g./100ft | 0.12
Density of Air | ρ | kg/m3 | 1.2
|  | Pa/m | 0.984
Duct Width or Height (Manual Entry for both H & W) | W or H | mm | (Enter Value to Override)
Duct Width or Height (Auto-Computed Length for one side) | W or H | mm | 250 | x | 385.4856 | (Exact; Computed Value)
|  | inch | 10 | x | 15.4194 | (Exact; Computed Value)
|  | mm | 250 | x | 400 | (Round-up; Computed Value)
|  | inch | 10 | x | 16 | (Round-up; Computed Value)
Match Column ID Position |  |  | 5
Match Closest Smaller Number |  |  | 0.88859
Match Row ID Position |  |  | 93
Other Key Information: |  | Showing Results for : | Rounded Value
|  | Selected Value : | 400
Equivalent Diameter | De | mm | 356.8248
|  | inch | 14.0482
Air Velocity | Vc | FPM | 929.368
Hydraulic Diameter | Dh | mm | 307.6923
Reynolds Number | Re | - | 96368.3157
Friction Factor (First Est.) | f' | - | 0.020444
Friction Factor | f | - | 0.020444
Velocity Pressure | Vp | "w.g. | 0.053848
Friction Loss per unit length | ΔP/L | Pa/m | 0.88859
|  | "w.g./100ft | 0.10836
Length of Duct | L | m | 10
Pressure Drop | ΔP | Pa | 8.8859
|  | "w.g. | 0.035544
Check: | ΔP/L | Pa/m | 0.96885
|  | "w.g./100ft | 0.11815

## Reference (hidden)
H\W | 50 | 100 | 150 | 200 | 250 | 300 | 350 | 400 | 450 | 500 | 550 | 600 | 650 | 700 | 750 | 800 | 850 | 900 | 950 | 1000 | 1050 | 1100 | 1150 | 1200 | 1250 | 1300 | 1350 | 1400 | 1450 | 1500 | 1550 | 1600 | 1650 | 1700 | 1750 | 1800 | 1850 | 1900 | 1950 | 2000 | 2050 | 2100 | 2150 | 2200 | 2250 | 2300 | 2350 | 2400 | 2450 | 2500 | 2550 | 2600 | 2650 | 2700 | 2750 | 2800 | 2850 | 2900 | 2950 | 3000 | 3050 | 3100 | 3150 | 3200 | 3250 | 3300 | 3350 | 3400 | 3450 | 3500 | 3550 | 3600 | 3650 | 3700 | 3750 | 3800 | 3850 | 3900 | 3950 | 4000 | 4050 | 4100 | 4150 | 4200 | 4250 | 4300 | 4350 | 4400 | 4450 | 4500 | 4550 | 4600 | 4650 | 4700 | 4750 | 4800 | 4850 | 4900 | 4950 | 5000 | 5050 | 250 | 0.984
5000 | 0.68757 | 0.084555 | 0.0251 | 0.010661 | 0.0055061 | 0.0032173 | 0.0020467 | 0.0013855 | 0.00098348 | 0.00072464 | 0.00055029 | 0.00042843 | 0.00034059 | 0.00027561 | 0.00022647 | 0.00018858 | 0.00015888 | 0.00013524 | 0.00011619 | 0.00010065 | 8.7835e-05 | 7.7172e-05 | 6.8221e-05 | 6.0647e-05 | 5.4192e-05 | 4.8654e-05 | 4.3873e-05 | 3.9722e-05 | 3.6099e-05 | 3.2922e-05 | 3.0123e-05 | 2.7646e-05 | 2.5445e-05 | 2.3483e-05 | 2.1727e-05 | 2.015e-05 | 1.873e-05 | 1.7447e-05 | 1.6284e-05 | 1.5228e-05 | 1.4267e-05 | 1.3389e-05 | 1.2586e-05 | 1.1849e-05 | 1.1173e-05 | 1.055e-05 | 9.975e-06 | 9.4439e-06 | 8.9522e-06 | 8.4962e-06 | 8.0728e-06 | 7.6788e-06 | 7.3118e-06 | 6.9694e-06 | 6.6496e-06 | 6.3504e-06 | 6.0702e-06 | 5.8074e-06 | 5.5606e-06 | 5.3287e-06 | 5.1104e-06 | 4.9049e-06 | 4.711e-06 | 4.528e-06 | 4.3551e-06 | 4.1916e-06 | 4.0369e-06 | 3.8902e-06 | 3.7512e-06 | 3.6193e-06 | 3.4939e-06 | 3.3748e-06 | 3.2615e-06 | 3.1537e-06 | 3.051e-06 | 2.953e-06 | 2.8596e-06 | 2.7704e-06 | 2.6853e-06 | 2.6039e-06 | 2.526e-06 | 2.4515e-06 | 2.3802e-06 | 2.3119e-06 | 2.2464e-06 | 2.1836e-06 | 2.1233e-06 | 2.0654e-06 | 2.0099e-06 | 1.9565e-06 | 1.9051e-06 | 1.8557e-06 | 1.8082e-06 | 1.7624e-06 | 1.7184e-06 | 1.6759e-06 | 1.6349e-06 | 1.5955e-06 | 1.5574e-06 | 1.5206e-06 | 1.4851e-06 | 0.0055061
4950 | 0.70024 | 0.086103 | 0.02556 | 0.010857 | 0.0056079 | 0.0032771 | 0.002085 | 0.0014116 | 0.001002 | 0.0007384 | 0.00056079 | 0.00043664 | 0.00034715 | 0.00028095 | 0.00023088 | 0.00019227 | 0.000162 | 0.00013791 | 0.00011849 | 0.00010265 | 8.9592e-05 | 7.8723e-05 | 6.9598e-05 | 6.1876e-05 | 5.5294e-05 | 4.9647e-05 | 4.4772e-05 | 4.0539e-05 | 3.6845e-05 | 3.3605e-05 | 3.0749e-05 | 2.8223e-05 | 2.5978e-05 | 2.3976e-05 | 2.2185e-05 | 2.0576e-05 | 1.9127e-05 | 1.7818e-05 | 1.6632e-05 | 1.5555e-05 | 1.4574e-05 | 1.3678e-05 | 1.2858e-05 | 1.2106e-05 | 1.1416e-05 | 1.078e-05 | 1.0193e-05 | 9.651e-06 | 9.149e-06 | 8.6835e-06 | 8.2512e-06 | 7.8489e-06 | 7.4742e-06 | 7.1246e-06 | 6.798e-06 | 6.4925e-06 | 6.2063e-06 | 5.9379e-06 | 5.6859e-06 | 5.449e-06 | 5.2261e-06 | 5.0161e-06 | 4.818e-06 | 4.6311e-06 | 4.4545e-06 | 4.2875e-06 | 4.1293e-06 | 3.9795e-06 | 3.8375e-06 | 3.7027e-06 | 3.5746e-06 | 3.4529e-06 | 3.3371e-06 | 3.2269e-06 | 3.1219e-06 | 3.0219e-06 | 2.9264e-06 | 2.8352e-06 | 2.7482e-06 | 2.665e-06 | 2.5854e-06 | 2.5093e-06 | 2.4363e-06 | 2.3665e-06 | 2.2995e-06 | 2.2353e-06 | 2.1737e-06 | 2.1145e-06 | 2.0577e-06 | 2.0031e-06 | 1.9506e-06 | 1.9001e-06 | 1.8515e-06 | 1.8047e-06 | 1.7596e-06 | 1.7162e-06 | 1.6743e-06 | 1.6339e-06 | 1.595e-06 | 1.5574e-06 | 1.521e-06 | 0.0056079
4900 | 0.71328 | 0.087696 | 0.026034 | 0.011059 | 0.0057127 | 0.0033386 | 0.0021244 | 0.0014384 | 0.0010212 | 0.00075257 | 0.00057161 | 0.00044511 | 0.00035392 | 0.00028645 | 0.00023542 | 0.00019607 | 0.00016522 | 0.00014067 | 0.00012087 | 0.00010472 | 9.1405e-05 | 8.0323e-05 | 7.1018e-05 | 6.3144e-05 | 5.6432e-05 | 5.0673e-05 | 4.57e-05 | 4.1383e-05 | 3.7615e-05 | 3.4309e-05 | 3.1397e-05 | 2.8819e-05 | 2.6529e-05 | 2.4486e-05 | 2.2658e-05 | 2.1017e-05 | 1.9538e-05 | 1.8202e-05 | 1.6992e-05 | 1.5892e-05 | 1.489e-05 | 1.3976e-05 | 1.3139e-05 | 1.2372e-05 | 1.1667e-05 | 1.1018e-05 | 1.0419e-05 | 9.8651e-06 | 9.3525e-06 | 8.8772e-06 | 8.4356e-06 | 8.0249e-06 | 7.6422e-06 | 7.2851e-06 | 6.9515e-06 | 6.6394e-06 | 6.3471e-06 | 6.0729e-06 | 5.8154e-06 | 5.5734e-06 | 5.3457e-06 | 5.1311e-06 | 4.9288e-06 | 4.7378e-06 | 4.5573e-06 | 4.3866e-06 | 4.2251e-06 | 4.072e-06 | 3.9268e-06 | 3.789e-06 | 3.6581e-06 | 3.5337e-06 | 3.4154e-06 | 3.3027e-06 | 3.1954e-06 | 3.0931e-06 | 2.9955e-06 | 2.9023e-06 | 2.8133e-06 | 2.7282e-06 | 2.6469e-06 | 2.569e-06 | 2.4945e-06 | 2.423e-06 | 2.3546e-06 | 2.2889e-06 | 2.2259e-06 | 2.1654e-06 | 2.1073e-06 | 2.0514e-06 | 1.9977e-06 | 1.9461e-06 | 1.8963e-06 | 1.8485e-06 | 1.8024e-06 | 1.7579e-06 | 1.7151e-06 | 1.6738e-06 | 1.6339e-06 | 1.5955e-06 | 1.5583e-06 | 0.0057127
4850 | 0.72671 | 0.089335 | 0.026521 | 0.011267 | 0.0058206 | 0.003402 | 0.0021649 | 0.001466 | 0.0010409 | 0.00076717 | 0.00058276 | 0.00045383 | 0.00036089 | 0.00029212 | 0.0002401 | 0.00019999 | 0.00016854 | 0.00014351 | 0.00012332 | 0.00010685 | 9.3275e-05 | 8.1973e-05 | 7.2483e-05 | 6.4452e-05 | 5.7606e-05 | 5.1731e-05 | 4.6659e-05 | 4.2254e-05 | 3.841e-05 | 3.5037e-05 | 3.2065e-05 | 2.9435e-05 | 2.7098e-05 | 2.5013e-05 | 2.3147e-05 | 2.1472e-05 | 1.9963e-05 | 1.8599e-05 | 1.7363e-05 | 1.6241e-05 | 1.5218e-05 | 1.4284e-05 | 1.343e-05 | 1.2647e-05 | 1.1927e-05 | 1.1264e-05 | 1.0652e-05 | 1.0086e-05 | 9.5629e-06 | 9.0774e-06 | 8.6264e-06 | 8.2068e-06 | 7.8159e-06 | 7.4511e-06 | 7.1103e-06 | 6.7914e-06 | 6.4927e-06 | 6.2126e-06 | 5.9495e-06 | 5.7022e-06 | 5.4695e-06 | 5.2502e-06 | 5.0434e-06 | 4.8482e-06 | 4.6638e-06 | 4.4893e-06 | 4.3241e-06 | 4.1677e-06 | 4.0192e-06 | 3.8784e-06 | 3.7446e-06 | 3.6174e-06 | 3.4964e-06 | 3.3812e-06 | 3.2715e-06 | 3.1669e-06 | 3.0671e-06 | 2.9718e-06 | 2.8808e-06 | 2.7938e-06 | 2.7106e-06 | 2.6309e-06 | 2.5547e-06 | 2.4816e-06 | 2.4116e-06 | 2.3444e-06 | 2.28e-06 | 2.2181e-06 | 2.1586e-06 | 2.1015e-06 | 2.0465e-06 | 1.9937e-06 | 1.9428e-06 | 1.8939e-06 | 1.8467e-06 | 1.8012e-06 | 1.7574e-06 | 1.7151e-06 | 1.6743e-06 | 1.6349e-06 | 1.5969e-06 | 0.0058206
4800 | 0.74053 | 0.091024 | 0.027023 | 0.011481 | 0.0059317 | 0.0034673 | 0.0022067 | 0.0014944 | 0.0010612 | 0.00078221 | 0.00059425 | 0.00046283 | 0.00036808 | 0.00029797 | 0.00024494 | 0.00020404 | 0.00017196 | 0.00014644 | 0.00012585 | 0.00010905 | 9.5206e-05 | 8.3677e-05 | 7.3997e-05 | 6.5803e-05 | 5.8819e-05 | 5.2825e-05 | 4.7649e-05 | 4.3154e-05 | 3.9231e-05 | 3.5789e-05 | 3.2755e-05 | 3.0071e-05 | 2.7685e-05 | 2.5558e-05 | 2.3653e-05 | 2.1942e-05 | 2.0401e-05 | 1.9009e-05 | 1.7747e-05 | 1.6601e-05 | 1.5557e-05 | 1.4603e-05 | 1.3731e-05 | 1.2931e-05 | 1.2195e-05 | 1.1518e-05 | 1.0893e-05 | 1.0315e-05 | 9.7807e-06 | 9.2846e-06 | 8.8239e-06 | 8.3951e-06 | 7.9957e-06 | 7.6229e-06 | 7.2746e-06 | 6.9488e-06 | 6.6435e-06 | 6.3572e-06 | 6.0883e-06 | 5.8356e-06 | 5.5977e-06 | 5.3735e-06 | 5.1622e-06 | 4.9626e-06 | 4.774e-06 | 4.5956e-06 | 4.4268e-06 | 4.2668e-06 | 4.115e-06 | 3.971e-06 | 3.8342e-06 | 3.7041e-06 | 3.5804e-06 | 3.4626e-06 | 3.3503e-06 | 3.2433e-06 | 3.1412e-06 | 3.0438e-06 | 2.9507e-06 | 2.8617e-06 | 2.7766e-06 | 2.6951e-06 | 2.6171e-06 | 2.5423e-06 | 2.4707e-06 | 2.402e-06 | 2.336e-06 | 2.2727e-06 | 2.2119e-06 | 2.1534e-06 | 2.0972e-06 | 2.0431e-06 | 1.991e-06 | 1.9409e-06 | 1.8926e-06 | 1.8461e-06 | 1.8012e-06 | 1.7579e-06 | 1.7162e-06 | 1.6759e-06 | 1.637e-06 | 0.0059317
4750 | 0.75477 | 0.092762 | 0.02754 | 0.011701 | 0.0060462 | 0.0035346 | 0.0022497 | 0.0015237 | 0.0010821 | 0.00079773 | 0.0006061 | 0.00047211 | 0.0003755 | 0.00030401 | 0.00024992 | 0.00020821 | 0.0001755 | 0.00014946 | 0.00012846 | 0.00011133 | 9.7199e-05 | 8.5437e-05 | 7.5559e-05 | 6.7199e-05 | 6.0071e-05 | 5.3954e-05 | 4.8672e-05 | 4.4084e-05 | 4.0079e-05 | 3.6566e-05 | 3.3469e-05 | 3.0728e-05 | 2.8293e-05 | 2.612e-05 | 2.4176e-05 | 2.2429e-05 | 2.0855e-05 | 1.9433e-05 | 1.8145e-05 | 1.6974e-05 | 1.5907e-05 | 1.4933e-05 | 1.4042e-05 | 1.3225e-05 | 1.2473e-05 | 1.1781e-05 | 1.1143e-05 | 1.0553e-05 | 1.0006e-05 | 9.4991e-06 | 9.0282e-06 | 8.5901e-06 | 8.1818e-06 | 7.8008e-06 | 7.4448e-06 | 7.1117e-06 | 6.7996e-06 | 6.5069e-06 | 6.2321e-06 | 5.9737e-06 | 5.7304e-06 | 5.5013e-06 | 5.2851e-06 | 5.081e-06 | 4.8882e-06 | 4.7058e-06 | 4.5331e-06 | 4.3694e-06 | 4.2142e-06 | 4.0669e-06 | 3.927e-06 | 3.7939e-06 | 3.6674e-06 | 3.5469e-06 | 3.432e-06 | 3.3226e-06 | 3.2181e-06 | 3.1184e-06 | 3.0231e-06 | 2.9321e-06 | 2.845e-06 | 2.7616e-06 | 2.6818e-06 | 2.6053e-06 | 2.532e-06 | 2.4616e-06 | 2.3941e-06 | 2.3293e-06 | 2.267e-06 | 2.2072e-06 | 2.1496e-06 | 2.0943e-06 | 2.041e-06 | 1.9897e-06 | 1.9402e-06 | 1.8926e-06 | 1.8467e-06 | 1.8024e-06 | 1.7596e-06 | 1.7184e-06 | 1.6785e-06 | 0.0060462
4700 | 0.76945 | 0.094554 | 0.028073 | 0.011929 | 0.0061642 | 0.003604 | 0.0022941 | 0.001554 | 0.0011037 | 0.00081373 | 0.00061832 | 0.00048168 | 0.00038315 | 0.00031024 | 0.00025507 | 0.00021252 | 0.00017915 | 0.00015258 | 0.00013116 | 0.00011368 | 9.9258e-05 | 8.7254e-05 | 7.7174e-05 | 6.8641e-05 | 6.1365e-05 | 5.5121e-05 | 4.9729e-05 | 4.5045e-05 | 4.0957e-05 | 3.7369e-05 | 3.4207e-05 | 3.1409e-05 | 2.8921e-05 | 2.6702e-05 | 2.4716e-05 | 2.2932e-05 | 2.1325e-05 | 1.9872e-05 | 1.8556e-05 | 1.7359e-05 | 1.627e-05 | 1.5275e-05 | 1.4364e-05 | 1.3529e-05 | 1.2761e-05 | 1.2054e-05 | 1.1401e-05 | 1.0798e-05 | 1.0239e-05 | 9.7212e-06 | 9.2398e-06 | 8.7919e-06 | 8.3745e-06 | 7.985e-06 | 7.621e-06 | 7.2805e-06 | 6.9614e-06 | 6.6621e-06 | 6.381e-06 | 6.1167e-06 | 5.868e-06 | 5.6336e-06 | 5.4125e-06 | 5.2038e-06 | 5.0065e-06 | 4.8199e-06 | 4.6433e-06 | 4.4759e-06 | 4.3171e-06 | 4.1664e-06 | 4.0232e-06 | 3.8871e-06 | 3.7575e-06 | 3.6342e-06 | 3.5167e-06 | 3.4047e-06 | 3.2978e-06 | 3.1958e-06 | 3.0983e-06 | 3.0051e-06 | 2.9159e-06 | 2.8306e-06 | 2.7489e-06 | 2.6706e-06 | 2.5955e-06 | 2.5235e-06 | 2.4544e-06 | 2.3881e-06 | 2.3243e-06 | 2.263e-06 | 2.2041e-06 | 2.1474e-06 | 2.0928e-06 | 2.0403e-06 | 1.9897e-06 | 1.9409e-06 | 1.8939e-06 | 1.8485e-06 | 1.8047e-06 | 1.7624e-06 | 1.7216e-06 | 0.0061642
4650 | 0.78457 | 0.096401 | 0.028622 | 0.012163 | 0.0062859 | 0.0036755 | 0.0023399 | 0.0015851 | 0.001126 | 0.00083024 | 0.00063093 | 0.00049156 | 0.00039105 | 0.00031667 | 0.00026038 | 0.00021697 | 0.00018292 | 0.00015581 | 0.00013394 | 0.0001161 | 0.00010139 | 8.9133e-05 | 7.8842e-05 | 7.0131e-05 | 6.2703e-05 | 5.6328e-05 | 5.0822e-05 | 4.6039e-05 | 4.1864e-05 | 3.82e-05 | 3.4971e-05 | 3.2112e-05 | 2.9571e-05 | 2.7305e-05 | 2.5276e-05 | 2.3453e-05 | 2.1811e-05 | 2.0326e-05 | 1.8981e-05 | 1.7759e-05 | 1.6645e-05 | 1.5628e-05 | 1.4697e-05 | 1.3844e-05 | 1.3059e-05 | 1.2336e-05 | 1.1669e-05 | 1.1052e-05 | 1.0481e-05 | 9.9513e-06 | 9.4591e-06 | 9.0011e-06 | 8.5743e-06 | 8.1759e-06 | 7.8037e-06 | 7.4554e-06 | 7.129e-06 | 6.8229e-06 | 6.5354e-06 | 6.265e-06 | 6.0106e-06 | 5.7708e-06 | 5.5446e-06 | 5.3311e-06 | 5.1292e-06 | 4.9383e-06 | 4.7575e-06 | 4.5862e-06 | 4.4237e-06 | 4.2695e-06 | 4.123e-06 | 3.9836e-06 | 3.8511e-06 | 3.7249e-06 | 3.6046e-06 | 3.4899e-06 | 3.3805e-06 | 3.276e-06 | 3.1762e-06 | 3.0808e-06 | 2.9895e-06 | 2.9022e-06 | 2.8185e-06 | 2.7383e-06 | 2.6615e-06 | 2.5877e-06 | 2.517e-06 | 2.449e-06 | 2.3837e-06 | 2.321e-06 | 2.2606e-06 | 2.2026e-06 | 2.1467e-06 | 2.0928e-06 | 2.041e-06 | 1.991e-06 | 1.9428e-06 | 1.8963e-06 | 1.8515e-06 | 1.8082e-06 | 1.7664e-06 | 0.0062859
4600 | 0.80017 | 0.098305 | 0.029189 | 0.012405 | 0.0064114 | 0.0037492 | 0.0023871 | 0.0016173 | 0.0011489 | 0.00084728 | 0.00064395 | 0.00050176 | 0.00039921 | 0.00032331 | 0.00026587 | 0.00022156 | 0.00018681 | 0.00015914 | 0.00013682 | 0.00011861 | 0.00010358 | 9.1074e-05 | 8.0567e-05 | 7.1672e-05 | 6.4087e-05 | 5.7576e-05 | 5.1952e-05 | 4.7068e-05 | 4.2802e-05 | 3.906e-05 | 3.5761e-05 | 3.284e-05 | 3.0244e-05 | 2.7928e-05 | 2.5855e-05 | 2.3992e-05 | 2.2314e-05 | 2.0797e-05 | 1.9422e-05 | 1.8172e-05 | 1.7034e-05 | 1.5994e-05 | 1.5043e-05 | 1.417e-05 | 1.3367e-05 | 1.2628e-05 | 1.1946e-05 | 1.1316e-05 | 1.0731e-05 | 1.019e-05 | 9.6863e-06 | 9.2178e-06 | 8.7813e-06 | 8.3738e-06 | 7.993e-06 | 7.6367e-06 | 7.3028e-06 | 6.9896e-06 | 6.6954e-06 | 6.4188e-06 | 6.1584e-06 | 5.9131e-06 | 5.6816e-06 | 5.4631e-06 | 5.2565e-06 | 5.0611e-06 | 4.8761e-06 | 4.7007e-06 | 4.5344e-06 | 4.3765e-06 | 4.2265e-06 | 4.0839e-06 | 3.9481e-06 | 3.8189e-06 | 3.6958e-06 | 3.5784e-06 | 3.4663e-06 | 3.3594e-06 | 3.2571e-06 | 3.1594e-06 | 3.066e-06 | 2.9765e-06 | 2.8908e-06 | 2.8087e-06 | 2.7299e-06 | 2.6544e-06 | 2.5819e-06 | 2.5123e-06 | 2.4454e-06 | 2.3811e-06 | 2.3193e-06 | 2.2598e-06 | 2.2026e-06 | 2.1474e-06 | 2.0943e-06 | 2.0431e-06 | 1.9937e-06 | 1.9461e-06 | 1.9001e-06 | 1.8557e-06 | 1.8129e-06 | 0.0064114
4550 | 0.81626 | 0.10027 | 0.029773 | 0.012654 | 0.0065408 | 0.0038254 | 0.0024358 | 0.0016505 | 0.0011727 | 0.00086487 | 0.0006574 | 0.00051229 | 0.00040763 | 0.00033017 | 0.00027154 | 0.00022631 | 0.00019083 | 0.00016259 | 0.0001398 | 0.0001212 | 0.00010586 | 9.3083e-05 | 8.2352e-05 | 7.3266e-05 | 6.5518e-05 | 5.8867e-05 | 5.3122e-05 | 4.8132e-05 | 4.3774e-05 | 3.995e-05 | 3.6578e-05 | 3.3594e-05 | 3.0941e-05 | 2.8574e-05 | 2.6454e-05 | 2.455e-05 | 2.2835e-05 | 2.1284e-05 | 1.9878e-05 | 1.8601e-05 | 1.7437e-05 | 1.6374e-05 | 1.5401e-05 | 1.4508e-05 | 1.3687e-05 | 1.2931e-05 | 1.2234e-05 | 1.1589e-05 | 1.0991e-05 | 1.0437e-05 | 9.9219e-06 | 9.4426e-06 | 8.9959e-06 | 8.579e-06 | 8.1894e-06 | 7.8247e-06 | 7.4831e-06 | 7.1625e-06 | 6.8614e-06 | 6.5783e-06 | 6.3118e-06 | 6.0607e-06 | 5.8237e-06 | 5.6e-06 | 5.3886e-06 | 5.1885e-06 | 4.9991e-06 | 4.8195e-06 | 4.6492e-06 | 4.4875e-06 | 4.3339e-06 | 4.1879e-06 | 4.0489e-06 | 3.9166e-06 | 3.7904e-06 | 3.6702e-06 | 3.5554e-06 | 3.4459e-06 | 3.3412e-06 | 3.2411e-06 | 3.1453e-06 | 3.0536e-06 | 2.9659e-06 | 2.8817e-06 | 2.8011e-06 | 2.7237e-06 | 2.6494e-06 | 2.5781e-06 | 2.5095e-06 | 2.4436e-06 | 2.3803e-06 | 2.3193e-06 | 2.2606e-06 | 2.2041e-06 | 2.1496e-06 | 2.0972e-06 | 2.0465e-06 | 1.9977e-06 | 1.9506e-06 | 1.9051e-06 | 1.8612e-06 | 0.0065408
4500 | 0.83286 | 0.10229 | 0.030375 | 0.012911 | 0.0066744 | 0.0039039 | 0.0024862 | 0.0016848 | 0.0011972 | 0.00088304 | 0.00067129 | 0.00052317 | 0.00041634 | 0.00033726 | 0.0002774 | 0.00023122 | 0.000195 | 0.00016615 | 0.00014288 | 0.00012388 | 0.00010821 | 9.516e-05 | 8.4198e-05 | 7.4916e-05 | 6.7e-05 | 6.0204e-05 | 5.4333e-05 | 4.9233e-05 | 4.478e-05 | 4.0871e-05 | 3.7425e-05 | 3.4374e-05 | 3.1662e-05 | 2.9242e-05 | 2.7076e-05 | 2.5129e-05 | 2.3375e-05 | 2.1789e-05 | 2.0351e-05 | 1.9045e-05 | 1.7854e-05 | 1.6767e-05 | 1.5772e-05 | 1.4859e-05 | 1.4019e-05 | 1.3246e-05 | 1.2532e-05 | 1.1872e-05 | 1.126e-05 | 1.0693e-05 | 1.0166e-05 | 9.6758e-06 | 9.2186e-06 | 8.7919e-06 | 8.3931e-06 | 8.0199e-06 | 7.6701e-06 | 7.342e-06 | 7.0338e-06 | 6.7439e-06 | 6.471e-06 | 6.2139e-06 | 5.9713e-06 | 5.7422e-06 | 5.5256e-06 | 5.3208e-06 | 5.1268e-06 | 4.9429e-06 | 4.7685e-06 | 4.6029e-06 | 4.4455e-06 | 4.2959e-06 | 4.1535e-06 | 4.018e-06 | 3.8888e-06 | 3.7656e-06 | 3.648e-06 | 3.5357e-06 | 3.4284e-06 | 3.3259e-06 | 3.2277e-06 | 3.1338e-06 | 3.0438e-06 | 2.9576e-06 | 2.8749e-06 | 2.7956e-06 | 2.7195e-06 | 2.6464e-06 | 2.5761e-06 | 2.5086e-06 | 2.4436e-06 | 2.3811e-06 | 2.321e-06 | 2.263e-06 | 2.2072e-06 | 2.1534e-06 | 2.1015e-06 | 2.0514e-06 | 2.0031e-06 | 1.9565e-06 | 1.9114e-06 | 0.0066744
4450 | 0.85 | 0.10438 | 0.030997 | 0.013176 | 0.0068123 | 0.003985 | 0.0025381 | 0.0017202 | 0.0012225 | 0.00090182 | 0.00068564 | 0.00053442 | 0.00042534 | 0.00034459 | 0.00028346 | 0.0002363 | 0.0001993 | 0.00016983 | 0.00014606 | 0.00012665 | 0.00011064 | 9.7311e-05 | 8.6109e-05 | 7.6624e-05 | 6.8534e-05 | 6.1588e-05 | 5.5588e-05 | 5.0374e-05 | 4.5822e-05 | 4.1826e-05 | 3.8303e-05 | 3.5183e-05 | 3.241e-05 | 2.9935e-05 | 2.772e-05 | 2.5729e-05 | 2.3934e-05 | 2.2312e-05 | 2.0842e-05 | 1.9505e-05 | 1.8287e-05 | 1.7175e-05 | 1.6157e-05 | 1.5222e-05 | 1.4363e-05 | 1.3572e-05 | 1.2841e-05 | 1.2166e-05 | 1.154e-05 | 1.0959e-05 | 1.042e-05 | 9.9178e-06 | 9.4498e-06 | 9.0129e-06 | 8.6046e-06 | 8.2224e-06 | 7.8643e-06 | 7.5283e-06 | 7.2127e-06 | 6.9158e-06 | 6.6364e-06 | 6.373e-06 | 6.1245e-06 | 5.8899e-06 | 5.668e-06 | 5.4582e-06 | 5.2594e-06 | 5.071e-06 | 4.8923e-06 | 4.7227e-06 | 4.5615e-06 | 4.4082e-06 | 4.2623e-06 | 4.1233e-06 | 3.9909e-06 | 3.8647e-06 | 3.7442e-06 | 3.6291e-06 | 3.5191e-06 | 3.414e-06 | 3.3134e-06 | 3.2171e-06 | 3.1249e-06 | 3.0365e-06 | 2.9518e-06 | 2.8704e-06 | 2.7924e-06 | 2.7174e-06 | 2.6454e-06 | 2.5761e-06 | 2.5095e-06 | 2.4454e-06 | 2.3837e-06 | 2.3243e-06 | 2.267e-06 | 2.2119e-06 | 2.1586e-06 | 2.1073e-06 | 2.0577e-06 | 2.0099e-06 | 1.9637e-06 | 0.0068123
4400 | 0.86769 | 0.10654 | 0.031639 | 0.01345 | 0.0069548 | 0.0040688 | 0.0025918 | 0.0017568 | 0.0012486 | 0.00092123 | 0.00070048 | 0.00054606 | 0.00043465 | 0.00035217 | 0.00028973 | 0.00024156 | 0.00020375 | 0.00017365 | 0.00014936 | 0.00012953 | 0.00011317 | 9.9538e-05 | 8.8089e-05 | 7.8393e-05 | 7.0123e-05 | 6.3022e-05 | 5.6887e-05 | 5.1557e-05 | 4.6901e-05 | 4.2815e-05 | 3.9212e-05 | 3.6022e-05 | 3.3185e-05 | 3.0654e-05 | 2.8387e-05 | 2.6351e-05 | 2.4515e-05 | 2.2855e-05 | 2.1351e-05 | 1.9983e-05 | 1.8737e-05 | 1.7598e-05 | 1.6556e-05 | 1.5599e-05 | 1.472e-05 | 1.391e-05 | 1.3162e-05 | 1.2471e-05 | 1.183e-05 | 1.1236e-05 | 1.0683e-05 | 1.0169e-05 | 9.6898e-06 | 9.2424e-06 | 8.8242e-06 | 8.4328e-06 | 8.066e-06 | 7.7218e-06 | 7.3985e-06 | 7.0944e-06 | 6.8081e-06 | 6.5383e-06 | 6.2837e-06 | 6.0433e-06 | 5.816e-06 | 5.6009e-06 | 5.3973e-06 | 5.2042e-06 | 5.0211e-06 | 4.8472e-06 | 4.682e-06 | 4.5248e-06 | 4.3753e-06 | 4.2329e-06 | 4.0971e-06 | 3.9677e-06 | 3.8442e-06 | 3.7262e-06 | 3.6134e-06 | 3.5057e-06 | 3.4025e-06 | 3.3038e-06 | 3.2092e-06 | 3.1186e-06 | 3.0316e-06 | 2.9482e-06 | 2.8682e-06 | 2.7913e-06 | 2.7174e-06 | 2.6464e-06 | 2.5781e-06 | 2.5123e-06 | 2.449e-06 | 2.3881e-06 | 2.3293e-06 | 2.2727e-06 | 2.2181e-06 | 2.1654e-06 | 2.1145e-06 | 2.0654e-06 | 2.018e-06 | 0.0069548
4350 | 0.88597 | 0.10877 | 0.032302 | 0.013734 | 0.007102 | 0.0041554 | 0.0026473 | 0.0017946 | 0.0012757 | 0.0009413 | 0.00071583 | 0.00055809 | 0.00044428 | 0.00036001 | 0.00029622 | 0.00024699 | 0.00020836 | 0.0001776 | 0.00015277 | 0.0001325 | 0.00011578 | 0.00010184 | 9.0139e-05 | 8.0226e-05 | 7.177e-05 | 6.4508e-05 | 5.8234e-05 | 5.2782e-05 | 4.8021e-05 | 4.3841e-05 | 4.0155e-05 | 3.6891e-05 | 3.3989e-05 | 3.1399e-05 | 2.908e-05 | 2.6996e-05 | 2.5117e-05 | 2.3418e-05 | 2.1878e-05 | 2.0479e-05 | 1.9203e-05 | 1.8037e-05 | 1.697e-05 | 1.5991e-05 | 1.5091e-05 | 1.4261e-05 | 1.3495e-05 | 1.2787e-05 | 1.2131e-05 | 1.1522e-05 | 1.0957e-05 | 1.043e-05 | 9.9391e-06 | 9.4808e-06 | 9.0524e-06 | 8.6514e-06 | 8.2756e-06 | 7.9229e-06 | 7.5916e-06 | 7.28e-06 | 6.9866e-06 | 6.7101e-06 | 6.4492e-06 | 6.2028e-06 | 5.9698e-06 | 5.7494e-06 | 5.5406e-06 | 5.3427e-06 | 5.1549e-06 | 4.9767e-06 | 4.8073e-06 | 4.6462e-06 | 4.4928e-06 | 4.3468e-06 | 4.2076e-06 | 4.0749e-06 | 3.9482e-06 | 3.8272e-06 | 3.7116e-06 | 3.601e-06 | 3.4952e-06 | 3.3939e-06 | 3.2969e-06 | 3.2039e-06 | 3.1148e-06 | 3.0292e-06 | 2.9471e-06 | 2.8682e-06 | 2.7924e-06 | 2.7195e-06 | 2.6494e-06 | 2.5819e-06 | 2.517e-06 | 2.4544e-06 | 2.3941e-06 | 2.336e-06 | 2.28e-06 | 2.2259e-06 | 2.1737e-06 | 2.1233e-06 | 2.0746e-06 | 0.007102
4300 | 0.90486 | 0.11108 | 0.032988 | 0.014026 | 0.0072541 | 0.004245 | 0.0027047 | 0.0018338 | 0.0013037 | 0.00096206 | 0.00073172 | 0.00057054 | 0.00045425 | 0.00036814 | 0.00030294 | 0.00025263 | 0.00021314 | 0.00018169 | 0.00015631 | 0.00013558 | 0.00011848 | 0.00010424 | 9.2265e-05 | 8.2126e-05 | 7.3477e-05 | 6.6049e-05 | 5.9631e-05 | 5.4054e-05 | 4.9182e-05 | 4.4905e-05 | 4.1134e-05 | 3.7793e-05 | 3.4824e-05 | 3.2173e-05 | 2.9799e-05 | 2.7665e-05 | 2.5742e-05 | 2.4003e-05 | 2.2427e-05 | 2.0993e-05 | 1.9687e-05 | 1.8494e-05 | 1.7401e-05 | 1.6398e-05 | 1.5476e-05 | 1.4626e-05 | 1.3842e-05 | 1.3116e-05 | 1.2444e-05 | 1.1821e-05 | 1.1241e-05 | 1.0701e-05 | 1.0198e-05 | 9.7286e-06 | 9.2896e-06 | 8.8786e-06 | 8.4935e-06 | 8.132e-06 | 7.7924e-06 | 7.473e-06 | 7.1723e-06 | 6.8888e-06 | 6.6213e-06 | 6.3686e-06 | 6.1298e-06 | 5.9038e-06 | 5.6897e-06 | 5.4868e-06 | 5.2942e-06 | 5.1114e-06 | 4.9376e-06 | 4.7724e-06 | 4.6151e-06 | 4.4653e-06 | 4.3226e-06 | 4.1864e-06 | 4.0564e-06 | 3.9323e-06 | 3.8137e-06 | 3.7002e-06 | 3.5917e-06 | 3.4878e-06 | 3.3882e-06 | 3.2928e-06 | 3.2013e-06 | 3.1135e-06 | 3.0292e-06 | 2.9482e-06 | 2.8704e-06 | 2.7956e-06 | 2.7237e-06 | 2.6544e-06 | 2.5877e-06 | 2.5235e-06 | 2.4616e-06 | 2.402e-06 | 2.3444e-06 | 2.2889e-06 | 2.2353e-06 | 2.1836e-06 | 2.1336e-06 | 0.0072541
4250 | 0.92439 | 0.11346 | 0.033696 | 0.014329 | 0.0074114 | 0.0043376 | 0.002764 | 0.0018742 | 0.0013326 | 0.00098355 | 0.00074815 | 0.00058343 | 0.00046457 | 0.00037655 | 0.0003099 | 0.00025846 | 0.00021809 | 0.00018593 | 0.00015997 | 0.00013878 | 0.00012129 | 0.00010671 | 9.4469e-05 | 8.4097e-05 | 7.5247e-05 | 6.7647e-05 | 6.108e-05 | 5.5373e-05 | 5.0387e-05 | 4.6009e-05 | 4.2149e-05 | 3.873e-05 | 3.569e-05 | 3.2976e-05 | 3.0545e-05 | 2.8361e-05 | 2.6391e-05 | 2.4611e-05 | 2.2996e-05 | 2.1528e-05 | 2.019e-05 | 1.8968e-05 | 1.7848e-05 | 1.6821e-05 | 1.5876e-05 | 1.5005e-05 | 1.4202e-05 | 1.3458e-05 | 1.277e-05 | 1.2131e-05 | 1.1536e-05 | 1.0983e-05 | 1.0468e-05 | 9.9864e-06 | 9.5363e-06 | 9.115e-06 | 8.7201e-06 | 8.3495e-06 | 8.0013e-06 | 7.6738e-06 | 7.3654e-06 | 7.0747e-06 | 6.8004e-06 | 6.5413e-06 | 6.2963e-06 | 6.0644e-06 | 5.8449e-06 | 5.6367e-06 | 5.4392e-06 | 5.2516e-06 | 5.0733e-06 | 4.9038e-06 | 4.7425e-06 | 4.5888e-06 | 4.4423e-06 | 4.3025e-06 | 4.1691e-06 | 4.0418e-06 | 3.92e-06 | 3.8036e-06 | 3.6922e-06 | 3.5855e-06 | 3.4833e-06 | 3.3854e-06 | 3.2914e-06 | 3.2013e-06 | 3.1148e-06 | 3.0316e-06 | 2.9518e-06 | 2.8749e-06 | 2.8011e-06 | 2.7299e-06 | 2.6615e-06 | 2.5955e-06 | 2.532e-06 | 2.4707e-06 | 2.4116e-06 | 2.3546e-06 | 2.2995e-06 | 2.2464e-06 | 2.195e-06 | 0.0074114
4200 | 0.94458 | 0.11592 | 0.034429 | 0.014642 | 0.0075741 | 0.0044333 | 0.0028254 | 0.0019161 | 0.0013626 | 0.0010058 | 0.00076518 | 0.00059679 | 0.00047526 | 0.00038526 | 0.00031711 | 0.00026451 | 0.00022321 | 0.00019032 | 0.00016377 | 0.00014209 | 0.00012419 | 0.00010929 | 9.6755e-05 | 8.6141e-05 | 7.7085e-05 | 6.9306e-05 | 6.2584e-05 | 5.6742e-05 | 5.1638e-05 | 4.7156e-05 | 4.3204e-05 | 3.9703e-05 | 3.6589e-05 | 3.381e-05 | 3.1321e-05 | 2.9083e-05 | 2.7066e-05 | 2.5242e-05 | 2.3588e-05 | 2.2084e-05 | 2.0713e-05 | 1.946e-05 | 1.8313e-05 | 1.726e-05 | 1.6292e-05 | 1.54e-05 | 1.4576e-05 | 1.3814e-05 | 1.3108e-05 | 1.2453e-05 | 1.1844e-05 | 1.1277e-05 | 1.0748e-05 | 1.0254e-05 | 9.793e-06 | 9.3609e-06 | 8.9559e-06 | 8.5759e-06 | 8.2187e-06 | 7.8828e-06 | 7.5664e-06 | 7.2682e-06 | 6.9868e-06 | 6.721e-06 | 6.4696e-06 | 6.2317e-06 | 6.0064e-06 | 5.7928e-06 | 5.5901e-06 | 5.3976e-06 | 5.2147e-06 | 5.0407e-06 | 4.8751e-06 | 4.7173e-06 | 4.5669e-06 | 4.4235e-06 | 4.2866e-06 | 4.1558e-06 | 4.0308e-06 | 3.9113e-06 | 3.7969e-06 | 3.6874e-06 | 3.5824e-06 | 3.4818e-06 | 3.3854e-06 | 3.2928e-06 | 3.2039e-06 | 3.1186e-06 | 3.0365e-06 | 2.9576e-06 | 2.8817e-06 | 2.8087e-06 | 2.7383e-06 | 2.6706e-06 | 2.6053e-06 | 2.5423e-06 | 2.4816e-06 | 2.423e-06 | 2.3665e-06 | 2.3119e-06 | 2.2591e-06 | 0.0075741
4150 | 0.96548 | 0.11847 | 0.035187 | 0.014965 | 0.0077425 | 0.0045325 | 0.002889 | 0.0019595 | 0.0013936 | 0.0010288 | 0.00078282 | 0.00061062 | 0.00048635 | 0.0003943 | 0.00032459 | 0.00027078 | 0.00022853 | 0.00019488 | 0.00016771 | 0.00014553 | 0.00012721 | 0.00011195 | 9.9129e-05 | 8.8264e-05 | 7.8993e-05 | 7.1029e-05 | 6.4146e-05 | 5.8164e-05 | 5.2937e-05 | 4.8347e-05 | 4.4299e-05 | 4.0713e-05 | 3.7524e-05 | 3.4677e-05 | 3.2127e-05 | 2.9834e-05 | 2.7767e-05 | 2.5898e-05 | 2.4203e-05 | 2.2662e-05 | 2.1257e-05 | 1.9973e-05 | 1.8797e-05 | 1.7718e-05 | 1.6725e-05 | 1.581e-05 | 1.4966e-05 | 1.4184e-05 | 1.346e-05 | 1.2788e-05 | 1.2164e-05 | 1.1582e-05 | 1.104e-05 | 1.0534e-05 | 1.006e-05 | 9.617e-06 | 9.2015e-06 | 8.8115e-06 | 8.4451e-06 | 8.1004e-06 | 7.7758e-06 | 7.4698e-06 | 7.181e-06 | 6.9081e-06 | 6.6502e-06 | 6.406e-06 | 6.1747e-06 | 5.9555e-06 | 5.7474e-06 | 5.5498e-06 | 5.362e-06 | 5.1833e-06 | 5.0133e-06 | 4.8513e-06 | 4.6969e-06 | 4.5496e-06 | 4.409e-06 | 4.2747e-06 | 4.1463e-06 | 4.0235e-06 | 3.906e-06 | 3.7935e-06 | 3.6857e-06 | 3.5824e-06 | 3.4833e-06 | 3.3882e-06 | 3.2969e-06 | 3.2092e-06 | 3.1249e-06 | 3.0438e-06 | 2.9659e-06 | 2.8908e-06 | 2.8185e-06 | 2.7489e-06 | 2.6818e-06 | 2.6171e-06 | 2.5547e-06 | 2.4945e-06 | 2.4363e-06 | 2.3802e-06 | 2.326e-06 | 0.0077425
4100 | 0.98711 | 0.1211 | 0.035971 | 0.015301 | 0.0079169 | 0.0046352 | 0.0029548 | 0.0020045 | 0.0014258 | 0.0010527 | 0.0008011 | 0.00062497 | 0.00049784 | 0.00040366 | 0.00033234 | 0.00027728 | 0.00023405 | 0.00019961 | 0.0001718 | 0.00014909 | 0.00013035 | 0.00011472 | 0.00010159 | 9.0468e-05 | 8.0974e-05 | 7.2818e-05 | 6.5769e-05 | 5.9642e-05 | 5.4287e-05 | 4.9586e-05 | 4.5438e-05 | 4.1764e-05 | 3.8496e-05 | 3.5579e-05 | 3.2965e-05 | 3.0615e-05 | 2.8497e-05 | 2.6581e-05 | 2.4843e-05 | 2.3263e-05 | 2.1822e-05 | 2.0506e-05 | 1.93e-05 | 1.8194e-05 | 1.7176e-05 | 1.6237e-05 | 1.5371e-05 | 1.457e-05 | 1.3827e-05 | 1.3138e-05 | 1.2497e-05 | 1.19e-05 | 1.1344e-05 | 1.0824e-05 | 1.0339e-05 | 9.8837e-06 | 9.4573e-06 | 9.0571e-06 | 8.681e-06 | 8.3272e-06 | 7.994e-06 | 7.6798e-06 | 7.3833e-06 | 7.1032e-06 | 6.8383e-06 | 6.5877e-06 | 6.3502e-06 | 6.125e-06 | 5.9113e-06 | 5.7084e-06 | 5.5155e-06 | 5.332e-06 | 5.1574e-06 | 4.991e-06 | 4.8324e-06 | 4.6811e-06 | 4.5366e-06 | 4.3986e-06 | 4.2667e-06 | 4.1406e-06 | 4.0199e-06 | 3.9043e-06 | 3.7935e-06 | 3.6874e-06 | 3.5855e-06 | 3.4878e-06 | 3.3939e-06 | 3.3038e-06 | 3.2171e-06 | 3.1338e-06 | 3.0536e-06 | 2.9765e-06 | 2.9022e-06 | 2.8306e-06 | 2.7616e-06 | 2.6951e-06 | 2.6309e-06 | 2.569e-06 | 2.5093e-06 | 2.4515e-06 | 2.3958e-06 | 0.0079169
4050 | 1.0095 | 0.12383 | 0.036783 | 0.015648 | 0.0080975 | 0.0047415 | 0.0030231 | 0.002051 | 0.0014591 | 0.0010775 | 0.00082005 | 0.00063984 | 0.00050976 | 0.00041338 | 0.00034039 | 0.00028403 | 0.00023978 | 0.00020452 | 0.00017605 | 0.0001528 | 0.0001336 | 0.0001176 | 0.00010415 | 9.2759e-05 | 8.3034e-05 | 7.4678e-05 | 6.7456e-05 | 6.1178e-05 | 5.5691e-05 | 5.0873e-05 | 4.6622e-05 | 4.2857e-05 | 3.9507e-05 | 3.6517e-05 | 3.3837e-05 | 3.1428e-05 | 2.9256e-05 | 2.7291e-05 | 2.5509e-05 | 2.3889e-05 | 2.2411e-05 | 2.1061e-05 | 1.9824e-05 | 1.8689e-05 | 1.7645e-05 | 1.6682e-05 | 1.5793e-05 | 1.4971e-05 | 1.4209e-05 | 1.3502e-05 | 1.2844e-05 | 1.2232e-05 | 1.1661e-05 | 1.1127e-05 | 1.0629e-05 | 1.0162e-05 | 9.7239e-06 | 9.313e-06 | 8.9269e-06 | 8.5636e-06 | 8.2214e-06 | 7.8988e-06 | 7.5943e-06 | 7.3066e-06 | 7.0346e-06 | 6.7771e-06 | 6.5332e-06 | 6.3019e-06 | 6.0824e-06 | 5.8739e-06 | 5.6757e-06 | 5.4872e-06 | 5.3077e-06 | 5.1368e-06 | 4.9738e-06 | 4.8183e-06 | 4.6698e-06 | 4.528e-06 | 4.3924e-06 | 4.2628e-06 | 4.1387e-06 | 4.0199e-06 | 3.906e-06 | 3.7969e-06 | 3.6922e-06 | 3.5917e-06 | 3.4952e-06 | 3.4025e-06 | 3.3134e-06 | 3.2277e-06 | 3.1453e-06 | 3.066e-06 | 2.9895e-06 | 2.9159e-06 | 2.845e-06 | 2.7766e-06 | 2.7106e-06 | 2.6469e-06 | 2.5854e-06 | 2.526e-06 | 2.4687e-06 | 0.0080975
4000 | 1.0327 | 0.12666 | 0.037625 | 0.016007 | 0.0082846 | 0.0048518 | 0.0030938 | 0.0020993 | 0.0014937 | 0.0011032 | 0.00083972 | 0.00065528 | 0.00052213 | 0.00042347 | 0.00034874 | 0.00029104 | 0.00024573 | 0.00020962 | 0.00018047 | 0.00015665 | 0.00013698 | 0.00012059 | 0.00010682 | 9.514e-05 | 8.5175e-05 | 7.6613e-05 | 6.9211e-05 | 6.2776e-05 | 5.7152e-05 | 5.2213e-05 | 4.7855e-05 | 4.3994e-05 | 4.0559e-05 | 3.7493e-05 | 3.4745e-05 | 3.2274e-05 | 3.0046e-05 | 2.8031e-05 | 2.6203e-05 | 2.4541e-05 | 2.3025e-05 | 2.1639e-05 | 2.037e-05 | 1.9205e-05 | 1.8134e-05 | 1.7146e-05 | 1.6233e-05 | 1.5389e-05 | 1.4607e-05 | 1.3881e-05 | 1.3206e-05 | 1.2577e-05 | 1.1991e-05 | 1.1443e-05 | 1.0931e-05 | 1.0452e-05 | 1.0002e-05 | 9.58e-06 | 9.1833e-06 | 8.8102e-06 | 8.4587e-06 | 8.1272e-06 | 7.8144e-06 | 7.5189e-06 | 7.2394e-06 | 6.9748e-06 | 6.7241e-06 | 6.4864e-06 | 6.2608e-06 | 6.0466e-06 | 5.8429e-06 | 5.6491e-06 | 5.4647e-06 | 5.2889e-06 | 5.1213e-06 | 4.9615e-06 | 4.8089e-06 | 4.6631e-06 | 4.5237e-06 | 4.3904e-06 | 4.2628e-06 | 4.1406e-06 | 4.0235e-06 | 3.9113e-06 | 3.8036e-06 | 3.7002e-06 | 3.601e-06 | 3.5057e-06 | 3.414e-06 | 3.3259e-06 | 3.2411e-06 | 3.1594e-06 | 3.0808e-06 | 3.0051e-06 | 2.9321e-06 | 2.8617e-06 | 2.7938e-06 | 2.7282e-06 | 2.665e-06 | 2.6039e-06 | 2.5448e-06 | 0.0082846
3950 | 1.0568 | 0.12959 | 0.038497 | 0.01638 | 0.0084786 | 0.0049661 | 0.0031671 | 0.0021494 | 0.0015295 | 0.0011298 | 0.00086014 | 0.00067131 | 0.00053497 | 0.00043395 | 0.00035742 | 0.00029832 | 0.00025191 | 0.00021492 | 0.00018505 | 0.00016065 | 0.0001405 | 0.00012371 | 0.00010958 | 9.7617e-05 | 8.7402e-05 | 7.8625e-05 | 7.1037e-05 | 6.4439e-05 | 5.8672e-05 | 5.3607e-05 | 4.9138e-05 | 4.5178e-05 | 4.1655e-05 | 3.8509e-05 | 3.569e-05 | 3.3156e-05 | 3.087e-05 | 2.8802e-05 | 2.6926e-05 | 2.522e-05 | 2.3664e-05 | 2.2242e-05 | 2.094e-05 | 1.9744e-05 | 1.8643e-05 | 1.7629e-05 | 1.6692e-05 | 1.5826e-05 | 1.5022e-05 | 1.4277e-05 | 1.3583e-05 | 1.2938e-05 | 1.2335e-05 | 1.1773e-05 | 1.1247e-05 | 1.0754e-05 | 1.0292e-05 | 9.8585e-06 | 9.451e-06 | 9.0675e-06 | 8.7063e-06 | 8.3657e-06 | 8.0442e-06 | 7.7404e-06 | 7.4531e-06 | 7.1812e-06 | 6.9235e-06 | 6.6791e-06 | 6.4472e-06 | 6.2269e-06 | 6.0175e-06 | 5.8183e-06 | 5.6286e-06 | 5.4478e-06 | 5.2755e-06 | 5.1111e-06 | 4.9541e-06 | 4.8042e-06 | 4.6608e-06 | 4.5237e-06 | 4.3924e-06 | 4.2667e-06 | 4.1463e-06 | 4.0308e-06 | 3.92e-06 | 3.8137e-06 | 3.7116e-06 | 3.6134e-06 | 3.5191e-06 | 3.4284e-06 | 3.3412e-06 | 3.2571e-06 | 3.1762e-06 | 3.0983e-06 | 3.0231e-06 | 2.9507e-06 | 2.8808e-06 | 2.8133e-06 | 2.7482e-06 | 2.6853e-06 | 2.6245e-06 | 0.0084786
3900 | 1.0817 | 0.13262 | 0.039401 | 0.016767 | 0.0086798 | 0.0050847 | 0.0032433 | 0.0022014 | 0.0015668 | 0.0011575 | 0.00088134 | 0.00068795 | 0.00054832 | 0.00044484 | 0.00036644 | 0.00030589 | 0.00025834 | 0.00022043 | 0.00018982 | 0.00016481 | 0.00014416 | 0.00012694 | 0.00011247 | 0.0001002 | 8.9721e-05 | 8.072e-05 | 7.2938e-05 | 6.617e-05 | 6.0255e-05 | 5.5059e-05 | 5.0475e-05 | 4.6412e-05 | 4.2797e-05 | 3.9569e-05 | 3.6676e-05 | 3.4074e-05 | 3.1728e-05 | 2.9605e-05 | 2.768e-05 | 2.5928e-05 | 2.4331e-05 | 2.2871e-05 | 2.1533e-05 | 2.0305e-05 | 1.9175e-05 | 1.8133e-05 | 1.7171e-05 | 1.6281e-05 | 1.5456e-05 | 1.469e-05 | 1.3977e-05 | 1.3314e-05 | 1.2695e-05 | 1.2117e-05 | 1.1576e-05 | 1.107e-05 | 1.0595e-05 | 1.0149e-05 | 9.7305e-06 | 9.3363e-06 | 8.965e-06 | 8.6148e-06 | 8.2842e-06 | 7.9719e-06 | 7.6765e-06 | 7.3968e-06 | 7.1318e-06 | 6.8805e-06 | 6.642e-06 | 6.4154e-06 | 6.2e-06 | 5.995e-06 | 5.7999e-06 | 5.614e-06 | 5.4367e-06 | 5.2675e-06 | 5.106e-06 | 4.9517e-06 | 4.8042e-06 | 4.6631e-06 | 4.528e-06 | 4.3986e-06 | 4.2747e-06 | 4.1558e-06 | 4.0418e-06 | 3.9323e-06 | 3.8272e-06 | 3.7262e-06 | 3.6291e-06 | 3.5357e-06 | 3.4459e-06 | 3.3594e-06 | 3.276e-06 | 3.1958e-06 | 3.1184e-06 | 3.0438e-06 | 2.9718e-06 | 2.9023e-06 | 2.8352e-06 | 2.7704e-06 | 2.7078e-06 | 0.0086798
3850 | 1.1076 | 0.13577 | 0.040339 | 0.017168 | 0.0088887 | 0.0052078 | 0.0033223 | 0.0022554 | 0.0016054 | 0.0011863 | 0.00090337 | 0.00070525 | 0.00056219 | 0.00045616 | 0.00037582 | 0.00031377 | 0.00026502 | 0.00022617 | 0.00019479 | 0.00016914 | 0.00014797 | 0.00013031 | 0.00011546 | 0.00010288 | 9.2136e-05 | 8.2902e-05 | 7.4918e-05 | 6.7975e-05 | 6.1905e-05 | 5.6573e-05 | 5.1868e-05 | 4.7698e-05 | 4.3987e-05 | 4.0673e-05 | 3.7703e-05 | 3.5032e-05 | 3.2623e-05 | 3.0444e-05 | 2.8466e-05 | 2.6667e-05 | 2.5026e-05 | 2.3527e-05 | 2.2153e-05 | 2.0891e-05 | 1.973e-05 | 1.866e-05 | 1.7671e-05 | 1.6756e-05 | 1.5908e-05 | 1.5121e-05 | 1.4389e-05 | 1.3706e-05 | 1.307e-05 | 1.2476e-05 | 1.192e-05 | 1.14e-05 | 1.0912e-05 | 1.0453e-05 | 1.0023e-05 | 9.6172e-06 | 9.2353e-06 | 8.8751e-06 | 8.5351e-06 | 8.2138e-06 | 7.9099e-06 | 7.6222e-06 | 7.3496e-06 | 7.091e-06 | 6.8456e-06 | 6.6124e-06 | 6.3908e-06 | 6.1798e-06 | 5.979e-06 | 5.7877e-06 | 5.6052e-06 | 5.4311e-06 | 5.2649e-06 | 5.106e-06 | 4.9541e-06 | 4.8089e-06 | 4.6698e-06 | 4.5366e-06 | 4.409e-06 | 4.2866e-06 | 4.1691e-06 | 4.0564e-06 | 3.9482e-06 | 3.8442e-06 | 3.7442e-06 | 3.648e-06 | 3.5554e-06 | 3.4663e-06 | 3.3805e-06 | 3.2978e-06 | 3.2181e-06 | 3.1412e-06 | 3.0671e-06 | 2.9955e-06 | 2.9264e-06 | 2.8596e-06 | 2.7951e-06 | 0.0088887
3800 | 1.1344 | 0.13904 | 0.041312 | 0.017584 | 0.0091055 | 0.0053356 | 0.0034044 | 0.0023115 | 0.0016456 | 0.0012161 | 0.00092627 | 0.00072324 | 0.00057662 | 0.00046794 | 0.00038558 | 0.00032196 | 0.00027198 | 0.00023214 | 0.00019996 | 0.00017366 | 0.00015193 | 0.00013382 | 0.00011859 | 0.00010568 | 9.4653e-05 | 8.5177e-05 | 7.6982e-05 | 6.9856e-05 | 6.3625e-05 | 5.8151e-05 | 5.3321e-05 | 4.9039e-05 | 4.5229e-05 | 4.1826e-05 | 3.8775e-05 | 3.6032e-05 | 3.3557e-05 | 3.1318e-05 | 2.9287e-05 | 2.7438e-05 | 2.5753e-05 | 2.4212e-05 | 2.28e-05 | 2.1503e-05 | 2.031e-05 | 1.9209e-05 | 1.8193e-05 | 1.7253e-05 | 1.6381e-05 | 1.5571e-05 | 1.4818e-05 | 1.4117e-05 | 1.3463e-05 | 1.2852e-05 | 1.228e-05 | 1.1745e-05 | 1.1243e-05 | 1.0771e-05 | 1.0328e-05 | 9.9108e-06 | 9.5179e-06 | 9.1473e-06 | 8.7974e-06 | 8.4668e-06 | 8.154e-06 | 7.8579e-06 | 7.5773e-06 | 7.3112e-06 | 7.0586e-06 | 6.8186e-06 | 6.5904e-06 | 6.3732e-06 | 6.1665e-06 | 5.9695e-06 | 5.7816e-06 | 5.6023e-06 | 5.4311e-06 | 5.2675e-06 | 5.1111e-06 | 4.9615e-06 | 4.8183e-06 | 4.6811e-06 | 4.5496e-06 | 4.4235e-06 | 4.3025e-06 | 4.1864e-06 | 4.0749e-06 | 3.9677e-06 | 3.8647e-06 | 3.7656e-06 | 3.6702e-06 | 3.5784e-06 | 3.4899e-06 | 3.4047e-06 | 3.3226e-06 | 3.2433e-06 | 3.1669e-06 | 3.0931e-06 | 3.0219e-06 | 2.953e-06 | 2.8865e-06 | 0.0091055
3750 | 1.1623 | 0.14244 | 0.042323 | 0.018016 | 0.0093307 | 0.0054685 | 0.0034897 | 0.0023698 | 0.0016874 | 0.0012472 | 0.00095009 | 0.00074196 | 0.00059163 | 0.00048019 | 0.00039574 | 0.00033049 | 0.00027923 | 0.00023836 | 0.00020534 | 0.00017836 | 0.00015607 | 0.00013748 | 0.00012185 | 0.00010859 | 9.7277e-05 | 8.7549e-05 | 7.9136e-05 | 7.1818e-05 | 6.542e-05 | 5.9798e-05 | 5.4837e-05 | 5.0439e-05 | 4.6525e-05 | 4.3029e-05 | 3.9895e-05 | 3.7076e-05 | 3.4533e-05 | 3.2232e-05 | 3.0144e-05 | 2.8244e-05 | 2.6511e-05 | 2.4927e-05 | 2.3475e-05 | 2.2142e-05 | 2.0915e-05 | 1.9784e-05 | 1.8739e-05 | 1.7772e-05 | 1.6875e-05 | 1.6042e-05 | 1.5268e-05 | 1.4546e-05 | 1.3873e-05 | 1.3244e-05 | 1.2656e-05 | 1.2105e-05 | 1.1589e-05 | 1.1103e-05 | 1.0647e-05 | 1.0218e-05 | 9.8136e-06 | 9.4321e-06 | 9.072e-06 | 8.7316e-06 | 8.4096e-06 | 8.1047e-06 | 7.8158e-06 | 7.5417e-06 | 7.2816e-06 | 7.0344e-06 | 6.7994e-06 | 6.5757e-06 | 6.3628e-06 | 6.1598e-06 | 5.9663e-06 | 5.7816e-06 | 5.6052e-06 | 5.4367e-06 | 5.2755e-06 | 5.1213e-06 | 4.9738e-06 | 4.8324e-06 | 4.6969e-06 | 4.5669e-06 | 4.4423e-06 | 4.3226e-06 | 4.2076e-06 | 4.0971e-06 | 3.9909e-06 | 3.8888e-06 | 3.7904e-06 | 3.6958e-06 | 3.6046e-06 | 3.5167e-06 | 3.432e-06 | 3.3503e-06 | 3.2715e-06 | 3.1954e-06 | 3.1219e-06 | 3.051e-06 | 2.9824e-06 | 0.0093307
3700 | 1.1913 | 0.14596 | 0.043373 | 0.018465 | 0.0095648 | 0.0056065 | 0.0035784 | 0.0024304 | 0.0017309 | 0.0012796 | 0.00097488 | 0.00076144 | 0.00060726 | 0.00049295 | 0.00040632 | 0.00033937 | 0.00028678 | 0.00024484 | 0.00021095 | 0.00018326 | 0.00016038 | 0.0001413 | 0.00012524 | 0.00011164 | 0.00010001 | 9.0024e-05 | 8.1383e-05 | 7.3866e-05 | 6.7293e-05 | 6.1518e-05 | 5.642e-05 | 5.1901e-05 | 4.7878e-05 | 4.4285e-05 | 4.1064e-05 | 3.8167e-05 | 3.5552e-05 | 3.3187e-05 | 3.104e-05 | 2.9086e-05 | 2.7305e-05 | 2.5675e-05 | 2.4182e-05 | 2.2811e-05 | 2.1549e-05 | 2.0385e-05 | 1.931e-05 | 1.8315e-05 | 1.7392e-05 | 1.6535e-05 | 1.5738e-05 | 1.4995e-05 | 1.4303e-05 | 1.3656e-05 | 1.305e-05 | 1.2483e-05 | 1.1951e-05 | 1.1451e-05 | 1.0982e-05 | 1.054e-05 | 1.0123e-05 | 9.7304e-06 | 9.3594e-06 | 9.0089e-06 | 8.6772e-06 | 8.3632e-06 | 8.0655e-06 | 7.7832e-06 | 7.5152e-06 | 7.2605e-06 | 7.0183e-06 | 6.7879e-06 | 6.5684e-06 | 6.3593e-06 | 6.1598e-06 | 5.9695e-06 | 5.7877e-06 | 5.614e-06 | 5.4478e-06 | 5.2889e-06 | 5.1368e-06 | 4.991e-06 | 4.8513e-06 | 4.7173e-06 | 4.5888e-06 | 4.4653e-06 | 4.3468e-06 | 4.2329e-06 | 4.1233e-06 | 4.018e-06 | 3.9166e-06 | 3.8189e-06 | 3.7249e-06 | 3.6342e-06 | 3.5469e-06 | 3.4626e-06 | 3.3812e-06 | 3.3027e-06 | 3.2269e-06 | 3.1537e-06 | 3.0829e-06 | 0.0095648
3650 | 1.2214 | 0.14963 | 0.044464 | 0.018932 | 0.0098082 | 0.0057501 | 0.0036706 | 0.0024935 | 0.0017761 | 0.0013132 | 0.0010007 | 0.00078173 | 0.00062354 | 0.00050625 | 0.00041734 | 0.00034864 | 0.00029465 | 0.00025159 | 0.00021681 | 0.00018837 | 0.00016487 | 0.00014528 | 0.00012879 | 0.00011481 | 0.00010287 | 9.2608e-05 | 8.3729e-05 | 7.6005e-05 | 6.925e-05 | 6.3314e-05 | 5.8074e-05 | 5.3428e-05 | 4.9293e-05 | 4.5599e-05 | 4.2286e-05 | 3.9307e-05 | 3.6618e-05 | 3.4185e-05 | 3.1977e-05 | 2.9967e-05 | 2.8134e-05 | 2.6458e-05 | 2.4922e-05 | 2.351e-05 | 2.2212e-05 | 2.1014e-05 | 1.9907e-05 | 1.8883e-05 | 1.7933e-05 | 1.7051e-05 | 1.623e-05 | 1.5466e-05 | 1.4752e-05 | 1.4086e-05 | 1.3462e-05 | 1.2878e-05 | 1.233e-05 | 1.1816e-05 | 1.1332e-05 | 1.0877e-05 | 1.0448e-05 | 1.0043e-05 | 9.6607e-06 | 9.2994e-06 | 8.9577e-06 | 8.634e-06 | 8.3273e-06 | 8.0363e-06 | 7.76e-06 | 7.4975e-06 | 7.2479e-06 | 7.0103e-06 | 6.7841e-06 | 6.5684e-06 | 6.3628e-06 | 6.1665e-06 | 5.979e-06 | 5.7999e-06 | 5.6286e-06 | 5.4647e-06 | 5.3077e-06 | 5.1574e-06 | 5.0133e-06 | 4.8751e-06 | 4.7425e-06 | 4.6151e-06 | 4.4928e-06 | 4.3753e-06 | 4.2623e-06 | 4.1535e-06 | 4.0489e-06 | 3.9481e-06 | 3.8511e-06 | 3.7575e-06 | 3.6674e-06 | 3.5804e-06 | 3.4964e-06 | 3.4154e-06 | 3.3371e-06 | 3.2615e-06 | 3.1885e-06 | 0.0098082
3600 | 1.2527 | 0.15344 | 0.0456 | 0.019418 | 0.010061 | 0.0058996 | 0.0037667 | 0.0025592 | 0.0018232 | 0.0013483 | 0.0010276 | 0.00080288 | 0.00064052 | 0.00052012 | 0.00042884 | 0.0003583 | 0.00030286 | 0.00025864 | 0.00022292 | 0.0001937 | 0.00016957 | 0.00014943 | 0.00013249 | 0.00011813 | 0.00010586 | 9.5308e-05 | 8.6181e-05 | 7.824e-05 | 7.1296e-05 | 6.5192e-05 | 5.9803e-05 | 5.5025e-05 | 5.0772e-05 | 4.6972e-05 | 4.3565e-05 | 4.05e-05 | 3.7733e-05 | 3.523e-05 | 3.2957e-05 | 3.0889e-05 | 2.9002e-05 | 2.7277e-05 | 2.5696e-05 | 2.4243e-05 | 2.2906e-05 | 2.1672e-05 | 2.0533e-05 | 1.9478e-05 | 1.85e-05 | 1.7591e-05 | 1.6746e-05 | 1.5959e-05 | 1.5224e-05 | 1.4537e-05 | 1.3895e-05 | 1.3293e-05 | 1.2728e-05 | 1.2198e-05 | 1.1699e-05 | 1.123e-05 | 1.0788e-05 | 1.0371e-05 | 9.9766e-06 | 9.6042e-06 | 9.2518e-06 | 8.9181e-06 | 8.6018e-06 | 8.3018e-06 | 8.0169e-06 | 7.7462e-06 | 7.4887e-06 | 7.2437e-06 | 7.0103e-06 | 6.7879e-06 | 6.5757e-06 | 6.3732e-06 | 6.1798e-06 | 5.995e-06 | 5.8183e-06 | 5.6491e-06 | 5.4872e-06 | 5.332e-06 | 5.1833e-06 | 5.0407e-06 | 4.9038e-06 | 4.7724e-06 | 4.6462e-06 | 4.5248e-06 | 4.4082e-06 | 4.2959e-06 | 4.1879e-06 | 4.0839e-06 | 3.9836e-06 | 3.8871e-06 | 3.7939e-06 | 3.7041e-06 | 3.6174e-06 | 3.5337e-06 | 3.4529e-06 | 3.3748e-06 | 3.2994e-06 | 0.010061
3550 | 1.2853 | 0.15741 | 0.046781 | 0.019924 | 0.010325 | 0.0060553 | 0.0038668 | 0.0026277 | 0.0018723 | 0.0013848 | 0.0010556 | 0.00082493 | 0.00065822 | 0.00053458 | 0.00044084 | 0.00036838 | 0.00031143 | 0.00026601 | 0.00022929 | 0.00019928 | 0.00017447 | 0.00015378 | 0.00013636 | 0.0001216 | 0.00010898 | 9.8131e-05 | 8.8745e-05 | 8.0578e-05 | 7.3435e-05 | 6.7156e-05 | 6.1613e-05 | 5.6697e-05 | 5.2321e-05 | 4.841e-05 | 4.4903e-05 | 4.1748e-05 | 3.8901e-05 | 3.6324e-05 | 3.3984e-05 | 3.1855e-05 | 2.9912e-05 | 2.8135e-05 | 2.6507e-05 | 2.501e-05 | 2.3633e-05 | 2.2363e-05 | 2.1189e-05 | 2.0102e-05 | 1.9094e-05 | 1.8158e-05 | 1.7287e-05 | 1.6475e-05 | 1.5718e-05 | 1.501e-05 | 1.4348e-05 | 1.3728e-05 | 1.3145e-05 | 1.2599e-05 | 1.2085e-05 | 1.1601e-05 | 1.1145e-05 | 1.0714e-05 | 1.0308e-05 | 9.924e-06 | 9.5605e-06 | 9.2163e-06 | 8.89e-06 | 8.5805e-06 | 8.2865e-06 | 8.0072e-06 | 7.7416e-06 | 7.4887e-06 | 7.2479e-06 | 7.0183e-06 | 6.7994e-06 | 6.5904e-06 | 6.3908e-06 | 6.2e-06 | 6.0175e-06 | 5.8429e-06 | 5.6757e-06 | 5.5155e-06 | 5.362e-06 | 5.2147e-06 | 5.0733e-06 | 4.9376e-06 | 4.8073e-06 | 4.682e-06 | 4.5615e-06 | 4.4455e-06 | 4.3339e-06 | 4.2265e-06 | 4.123e-06 | 4.0232e-06 | 3.927e-06 | 3.8342e-06 | 3.7446e-06 | 3.6581e-06 | 3.5746e-06 | 3.4939e-06 | 3.416e-06 | 0.010325
3500 | 1.3193 | 0.16153 | 0.048011 | 0.020451 | 0.0106 | 0.0062175 | 0.0039711 | 0.002699 | 0.0019235 | 0.001423 | 0.0010849 | 0.00084795 | 0.0006767 | 0.00054969 | 0.00045337 | 0.00037891 | 0.00032039 | 0.0002737 | 0.00023596 | 0.0002051 | 0.0001796 | 0.00015832 | 0.00014041 | 0.00012522 | 0.00011224 | 0.00010108 | 9.1428e-05 | 8.3025e-05 | 7.5674e-05 | 6.9213e-05 | 6.3507e-05 | 5.8447e-05 | 5.3942e-05 | 4.9916e-05 | 4.6305e-05 | 4.3057e-05 | 4.0124e-05 | 3.747e-05 | 3.506e-05 | 3.2867e-05 | 3.0865e-05 | 2.9035e-05 | 2.7357e-05 | 2.5815e-05 | 2.4396e-05 | 2.3086e-05 | 2.1876e-05 | 2.0756e-05 | 1.9717e-05 | 1.8752e-05 | 1.7854e-05 | 1.7017e-05 | 1.6236e-05 | 1.5507e-05 | 1.4824e-05 | 1.4184e-05 | 1.3583e-05 | 1.302e-05 | 1.2489e-05 | 1.199e-05 | 1.1519e-05 | 1.1075e-05 | 1.0656e-05 | 1.026e-05 | 9.8847e-06 | 9.5295e-06 | 9.1927e-06 | 8.8732e-06 | 8.5698e-06 | 8.2815e-06 | 8.0072e-06 | 7.7462e-06 | 7.4975e-06 | 7.2605e-06 | 7.0344e-06 | 6.8186e-06 | 6.6124e-06 | 6.4154e-06 | 6.2269e-06 | 6.0466e-06 | 5.8739e-06 | 5.7084e-06 | 5.5498e-06 | 5.3976e-06 | 5.2516e-06 | 5.1114e-06 | 4.9767e-06 | 4.8472e-06 | 4.7227e-06 | 4.6029e-06 | 4.4875e-06 | 4.3765e-06 | 4.2695e-06 | 4.1664e-06 | 4.0669e-06 | 3.971e-06 | 3.8784e-06 | 3.789e-06 | 3.7027e-06 | 3.6193e-06 | 3.5386e-06 | 0.0106
3450 | 1.3546 | 0.16584 | 0.049293 | 0.021 | 0.010886 | 0.0063865 | 0.0040798 | 0.0027735 | 0.0019769 | 0.0014628 | 0.0011154 | 0.00087198 | 0.000696 | 0.00056546 | 0.00046646 | 0.00038992 | 0.00032975 | 0.00028174 | 0.00024293 | 0.00021119 | 0.00018496 | 0.00016307 | 0.00014464 | 0.00012902 | 0.00011566 | 0.00010418 | 9.4238e-05 | 8.5587e-05 | 7.802e-05 | 7.1367e-05 | 6.5492e-05 | 6.0281e-05 | 5.5641e-05 | 5.1494e-05 | 4.7775e-05 | 4.4428e-05 | 4.1407e-05 | 3.8672e-05 | 3.6189e-05 | 3.3928e-05 | 3.1866e-05 | 2.9979e-05 | 2.8249e-05 | 2.6659e-05 | 2.5196e-05 | 2.3846e-05 | 2.2598e-05 | 2.1443e-05 | 2.0372e-05 | 1.9376e-05 | 1.845e-05 | 1.7587e-05 | 1.6781e-05 | 1.6028e-05 | 1.5323e-05 | 1.4663e-05 | 1.4044e-05 | 1.3462e-05 | 1.2914e-05 | 1.2399e-05 | 1.1913e-05 | 1.1455e-05 | 1.1022e-05 | 1.0613e-05 | 1.0226e-05 | 9.8587e-06 | 9.5109e-06 | 9.181e-06 | 8.8676e-06 | 8.5698e-06 | 8.2865e-06 | 8.0169e-06 | 7.76e-06 | 7.5152e-06 | 7.2816e-06 | 7.0586e-06 | 6.8456e-06 | 6.642e-06 | 6.4472e-06 | 6.2608e-06 | 6.0824e-06 | 5.9113e-06 | 5.7474e-06 | 5.5901e-06 | 5.4392e-06 | 5.2942e-06 | 5.1549e-06 | 5.0211e-06 | 4.8923e-06 | 4.7685e-06 | 4.6492e-06 | 4.5344e-06 | 4.4237e-06 | 4.3171e-06 | 4.2142e-06 | 4.115e-06 | 4.0192e-06 | 3.9268e-06 | 3.8375e-06 | 3.7512e-06 | 3.6678e-06 | 0.010886
3400 | 1.3915 | 0.17032 | 0.050629 | 0.021572 | 0.011185 | 0.006563 | 0.0041933 | 0.0028512 | 0.0020327 | 0.0015043 | 0.0011473 | 0.00089708 | 0.00071617 | 0.00058195 | 0.00048015 | 0.00040143 | 0.00033954 | 0.00029015 | 0.00025023 | 0.00021757 | 0.00019057 | 0.00016804 | 0.00014908 | 0.00013299 | 0.00011924 | 0.00010742 | 9.7181e-05 | 8.8273e-05 | 8.0478e-05 | 7.3625e-05 | 6.7573e-05 | 6.2204e-05 | 5.7423e-05 | 5.315e-05 | 4.9317e-05 | 4.5867e-05 | 4.2753e-05 | 3.9933e-05 | 3.7373e-05 | 3.5043e-05 | 3.2915e-05 | 3.097e-05 | 2.9186e-05 | 2.7546e-05 | 2.6037e-05 | 2.4644e-05 | 2.3357e-05 | 2.2165e-05 | 2.1059e-05 | 2.0032e-05 | 1.9076e-05 | 1.8185e-05 | 1.7353e-05 | 1.6576e-05 | 1.5849e-05 | 1.5167e-05 | 1.4527e-05 | 1.3926e-05 | 1.3361e-05 | 1.2829e-05 | 1.2327e-05 | 1.1854e-05 | 1.1407e-05 | 1.0984e-05 | 1.0584e-05 | 1.0205e-05 | 9.8457e-06 | 9.5048e-06 | 9.181e-06 | 8.8732e-06 | 8.5805e-06 | 8.3018e-06 | 8.0363e-06 | 7.7832e-06 | 7.5417e-06 | 7.3112e-06 | 7.091e-06 | 6.8805e-06 | 6.6791e-06 | 6.4864e-06 | 6.3019e-06 | 6.125e-06 | 5.9555e-06 | 5.7928e-06 | 5.6367e-06 | 5.4868e-06 | 5.3427e-06 | 5.2042e-06 | 5.071e-06 | 4.9429e-06 | 4.8195e-06 | 4.7007e-06 | 4.5862e-06 | 4.4759e-06 | 4.3694e-06 | 4.2668e-06 | 4.1677e-06 | 4.072e-06 | 3.9795e-06 | 3.8902e-06 | 3.8039e-06 | 0.011185
3350 | 1.43 | 0.175 | 0.052023 | 0.022169 | 0.011496 | 0.0067471 | 0.0043118 | 0.0029323 | 0.002091 | 0.0015478 | 0.0011807 | 0.00092334 | 0.00073727 | 0.0005992 | 0.00049447 | 0.00041348 | 0.00034979 | 0.00029896 | 0.00025787 | 0.00022425 | 0.00019645 | 0.00017326 | 0.00015373 | 0.00013716 | 0.000123 | 0.00011081 | 0.00010027 | 9.109e-05 | 8.3057e-05 | 7.5995e-05 | 6.9756e-05 | 6.4222e-05 | 5.9293e-05 | 5.4888e-05 | 5.0935e-05 | 4.7378e-05 | 4.4166e-05 | 4.1258e-05 | 3.8617e-05 | 3.6213e-05 | 3.4018e-05 | 3.2011e-05 | 3.017e-05 | 2.8478e-05 | 2.692e-05 | 2.5483e-05 | 2.4154e-05 | 2.2923e-05 | 2.1782e-05 | 2.0721e-05 | 1.9734e-05 | 1.8814e-05 | 1.7955e-05 | 1.7152e-05 | 1.6401e-05 | 1.5697e-05 | 1.5036e-05 | 1.4415e-05 | 1.3831e-05 | 1.3281e-05 | 1.2763e-05 | 1.2274e-05 | 1.1812e-05 | 1.1375e-05 | 1.0961e-05 | 1.057e-05 | 1.0198e-05 | 9.8457e-06 | 9.5109e-06 | 9.1927e-06 | 8.89e-06 | 8.6018e-06 | 8.3273e-06 | 8.0655e-06 | 7.8158e-06 | 7.5773e-06 | 7.3496e-06 | 7.1318e-06 | 6.9235e-06 | 6.7241e-06 | 6.5332e-06 | 6.3502e-06 | 6.1747e-06 | 6.0064e-06 | 5.8449e-06 | 5.6897e-06 | 5.5406e-06 | 5.3973e-06 | 5.2594e-06 | 5.1268e-06 | 4.9991e-06 | 4.8761e-06 | 4.7575e-06 | 4.6433e-06 | 4.5331e-06 | 4.4268e-06 | 4.3241e-06 | 4.2251e-06 | 4.1293e-06 | 4.0369e-06 | 3.9474e-06 | 0.011496
3300 | 1.4701 | 0.17988 | 0.053478 | 0.022793 | 0.011822 | 0.0069395 | 0.0044357 | 0.0030172 | 0.0021519 | 0.0015932 | 0.0012156 | 0.0009508 | 0.00075934 | 0.00061726 | 0.00050947 | 0.00042609 | 0.00036053 | 0.00030819 | 0.00026587 | 0.00023125 | 0.00020262 | 0.00017872 | 0.0001586 | 0.00014153 | 0.00012693 | 0.00011438 | 0.00010351 | 9.4046e-05 | 8.5765e-05 | 7.8483e-05 | 7.2049e-05 | 6.6342e-05 | 6.1258e-05 | 5.6713e-05 | 5.2636e-05 | 4.8966e-05 | 4.5652e-05 | 4.265e-05 | 3.9925e-05 | 3.7443e-05 | 3.5178e-05 | 3.3106e-05 | 3.1205e-05 | 2.9458e-05 | 2.7849e-05 | 2.6365e-05 | 2.4993e-05 | 2.3722e-05 | 2.2542e-05 | 2.1447e-05 | 2.0427e-05 | 1.9476e-05 | 1.8589e-05 | 1.7759e-05 | 1.6983e-05 | 1.6255e-05 | 1.5572e-05 | 1.493e-05 | 1.4327e-05 | 1.3758e-05 | 1.3222e-05 | 1.2716e-05 | 1.2238e-05 | 1.1787e-05 | 1.1359e-05 | 1.0954e-05 | 1.057e-05 | 1.0205e-05 | 9.8587e-06 | 9.5295e-06 | 9.2163e-06 | 8.9181e-06 | 8.634e-06 | 8.3632e-06 | 8.1047e-06 | 7.8579e-06 | 7.6222e-06 | 7.3968e-06 | 7.1812e-06 | 6.9748e-06 | 6.7771e-06 | 6.5877e-06 | 6.406e-06 | 6.2317e-06 | 6.0644e-06 | 5.9038e-06 | 5.7494e-06 | 5.6009e-06 | 5.4582e-06 | 5.3208e-06 | 5.1885e-06 | 5.0611e-06 | 4.9383e-06 | 4.8199e-06 | 4.7058e-06 | 4.5956e-06 | 4.4893e-06 | 4.3866e-06 | 4.2875e-06 | 4.1916e-06 | 4.099e-06 | 0.011822
3250 | 1.5121 | 0.18498 | 0.054998 | 0.023444 | 0.012162 | 0.0071406 | 0.0045652 | 0.0031059 | 0.0022157 | 0.0016407 | 0.0012521 | 0.00097957 | 0.00078247 | 0.00063618 | 0.00052518 | 0.00043932 | 0.00037178 | 0.00031787 | 0.00027427 | 0.00023859 | 0.00020909 | 0.00018446 | 0.00016372 | 0.00014612 | 0.00013107 | 0.00011812 | 0.00010691 | 9.7152e-05 | 8.861e-05 | 8.1097e-05 | 7.4459e-05 | 6.857e-05 | 6.3324e-05 | 5.8633e-05 | 5.4424e-05 | 5.0635e-05 | 4.7214e-05 | 4.4115e-05 | 4.1301e-05 | 3.8738e-05 | 3.6399e-05 | 3.4258e-05 | 3.2294e-05 | 3.049e-05 | 2.8828e-05 | 2.7294e-05 | 2.5876e-05 | 2.4562e-05 | 2.3343e-05 | 2.2211e-05 | 2.1157e-05 | 2.0174e-05 | 1.9256e-05 | 1.8399e-05 | 1.7596e-05 | 1.6843e-05 | 1.6137e-05 | 1.5473e-05 | 1.4849e-05 | 1.4261e-05 | 1.3706e-05 | 1.3183e-05 | 1.2688e-05 | 1.2221e-05 | 1.1778e-05 | 1.1359e-05 | 1.0961e-05 | 1.0584e-05 | 1.0226e-05 | 9.8847e-06 | 9.5605e-06 | 9.2518e-06 | 8.9577e-06 | 8.6772e-06 | 8.4096e-06 | 8.154e-06 | 7.9099e-06 | 7.6765e-06 | 7.4531e-06 | 7.2394e-06 | 7.0346e-06 | 6.8383e-06 | 6.6502e-06 | 6.4696e-06 | 6.2963e-06 | 6.1298e-06 | 5.9698e-06 | 5.816e-06 | 5.668e-06 | 5.5256e-06 | 5.3886e-06 | 5.2565e-06 | 5.1292e-06 | 5.0065e-06 | 4.8882e-06 | 4.774e-06 | 4.6638e-06 | 4.5573e-06 | 4.4545e-06 | 4.3551e-06 | 4.259e-06 | 0.012162
3200 | 1.556 | 0.1903 | 0.056587 | 0.024125 | 0.012518 | 0.007351 | 0.0047007 | 0.0031988 | 0.0022824 | 0.0016905 | 0.0012904 | 0.0010097 | 0.00080671 | 0.00065602 | 0.00054166 | 0.00045319 | 0.00038359 | 0.00032803 | 0.00028308 | 0.0002463 | 0.00021588 | 0.00019048 | 0.00016909 | 0.00015094 | 0.00013541 | 0.00012206 | 0.00011049 | 0.00010042 | 9.1601e-05 | 8.3846e-05 | 7.6994e-05 | 7.0914e-05 | 6.5497e-05 | 6.0653e-05 | 5.6306e-05 | 5.2393e-05 | 4.8859e-05 | 4.5657e-05 | 4.275e-05 | 4.0102e-05 | 3.7684e-05 | 3.5472e-05 | 3.3442e-05 | 3.1577e-05 | 2.9858e-05 | 2.8273e-05 | 2.6806e-05 | 2.5448e-05 | 2.4188e-05 | 2.3017e-05 | 2.1926e-05 | 2.091e-05 | 1.996e-05 | 1.9073e-05 | 1.8242e-05 | 1.7463e-05 | 1.6733e-05 | 1.6046e-05 | 1.5399e-05 | 1.4791e-05 | 1.4217e-05 | 1.3675e-05 | 1.3163e-05 | 1.2679e-05 | 1.2221e-05 | 1.1787e-05 | 1.1375e-05 | 1.0984e-05 | 1.0613e-05 | 1.026e-05 | 9.924e-06 | 9.6042e-06 | 9.2994e-06 | 9.0089e-06 | 8.7316e-06 | 8.4668e-06 | 8.2138e-06 | 7.9719e-06 | 7.7404e-06 | 7.5189e-06 | 7.3066e-06 | 7.1032e-06 | 6.9081e-06 | 6.721e-06 | 6.5413e-06 | 6.3686e-06 | 6.2028e-06 | 6.0433e-06 | 5.8899e-06 | 5.7422e-06 | 5.6e-06 | 5.4631e-06 | 5.3311e-06 | 5.2038e-06 | 5.081e-06 | 4.9626e-06 | 4.8482e-06 | 4.7378e-06 | 4.6311e-06 | 4.528e-06 | 4.4283e-06 | 0.012518
3150 | 1.6018 | 0.19588 | 0.058249 | 0.024838 | 0.01289 | 0.0075713 | 0.0048426 | 0.0032961 | 0.0023524 | 0.0017427 | 0.0013305 | 0.0010413 | 0.00083213 | 0.00067683 | 0.00055896 | 0.00046775 | 0.00039599 | 0.00033869 | 0.00029234 | 0.0002544 | 0.00022302 | 0.00019681 | 0.00017474 | 0.000156 | 0.00013998 | 0.00012619 | 0.00011425 | 0.00010385 | 9.4749e-05 | 8.674e-05 | 7.9662e-05 | 7.3381e-05 | 6.7785e-05 | 6.278e-05 | 5.8289e-05 | 5.4244e-05 | 5.0591e-05 | 4.7282e-05 | 4.4277e-05 | 4.1539e-05 | 3.9039e-05 | 3.6751e-05 | 3.4652e-05 | 3.2723e-05 | 3.0946e-05 | 2.9305e-05 | 2.7788e-05 | 2.6383e-05 | 2.5079e-05 | 2.3867e-05 | 2.2738e-05 | 2.1686e-05 | 2.0703e-05 | 1.9785e-05 | 1.8925e-05 | 1.8118e-05 | 1.7362e-05 | 1.665e-05 | 1.5981e-05 | 1.535e-05 | 1.4756e-05 | 1.4195e-05 | 1.3665e-05 | 1.3163e-05 | 1.2688e-05 | 1.2238e-05 | 1.1812e-05 | 1.1407e-05 | 1.1022e-05 | 1.0656e-05 | 1.0308e-05 | 9.9766e-06 | 9.6607e-06 | 9.3594e-06 | 9.072e-06 | 8.7974e-06 | 8.5351e-06 | 8.2842e-06 | 8.0442e-06 | 7.8144e-06 | 7.5943e-06 | 7.3833e-06 | 7.181e-06 | 6.9868e-06 | 6.8004e-06 | 6.6213e-06 | 6.4492e-06 | 6.2837e-06 | 6.1245e-06 | 5.9713e-06 | 5.8237e-06 | 5.6816e-06 | 5.5446e-06 | 5.4125e-06 | 5.2851e-06 | 5.1622e-06 | 5.0434e-06 | 4.9288e-06 | 4.818e-06 | 4.711e-06 | 4.6075e-06 | 0.01289
3100 | 1.6499 | 0.20171 | 0.059988 | 0.025584 | 0.01328 | 0.0078021 | 0.0049914 | 0.0033981 | 0.0024257 | 0.0017974 | 0.0013726 | 0.0010745 | 0.00085883 | 0.00069869 | 0.00057712 | 0.00048305 | 0.00040902 | 0.00034991 | 0.00030207 | 0.00026292 | 0.00023053 | 0.00020347 | 0.00018069 | 0.00016134 | 0.00014479 | 0.00013055 | 0.00011822 | 0.00010747 | 9.8065e-05 | 8.9789e-05 | 8.2474e-05 | 7.5982e-05 | 7.0197e-05 | 6.5023e-05 | 6.0379e-05 | 5.6197e-05 | 5.2419e-05 | 4.8996e-05 | 4.5887e-05 | 4.3055e-05 | 4.0469e-05 | 3.8101e-05 | 3.5929e-05 | 3.3933e-05 | 3.2093e-05 | 3.0395e-05 | 2.8825e-05 | 2.737e-05 | 2.6019e-05 | 2.4764e-05 | 2.3596e-05 | 2.2506e-05 | 2.1488e-05 | 2.0537e-05 | 1.9646e-05 | 1.881e-05 | 1.8026e-05 | 1.7289e-05 | 1.6596e-05 | 1.5942e-05 | 1.5326e-05 | 1.4744e-05 | 1.4195e-05 | 1.3675e-05 | 1.3183e-05 | 1.2716e-05 | 1.2274e-05 | 1.1854e-05 | 1.1455e-05 | 1.1075e-05 | 1.0714e-05 | 1.0371e-05 | 1.0043e-05 | 9.7304e-06 | 9.4321e-06 | 9.1473e-06 | 8.8751e-06 | 8.6148e-06 | 8.3657e-06 | 8.1272e-06 | 7.8988e-06 | 7.6798e-06 | 7.4698e-06 | 7.2682e-06 | 7.0747e-06 | 6.8888e-06 | 6.7101e-06 | 6.5383e-06 | 6.373e-06 | 6.2139e-06 | 6.0607e-06 | 5.9131e-06 | 5.7708e-06 | 5.6336e-06 | 5.5013e-06 | 5.3735e-06 | 5.2502e-06 | 5.1311e-06 | 5.0161e-06 | 4.9049e-06 | 4.7973e-06 | 0.01328
3050 | 1.7002 | 0.20782 | 0.061811 | 0.026366 | 0.013689 | 0.0080441 | 0.0051474 | 0.0035052 | 0.0025027 | 0.0018549 | 0.0014168 | 0.0011093 | 0.00088688 | 0.00072166 | 0.00059622 | 0.00049914 | 0.00042273 | 0.0003617 | 0.00031232 | 0.00027188 | 0.00023843 | 0.00021049 | 0.00018695 | 0.00016696 | 0.00014986 | 0.00013514 | 0.00012239 | 0.00011129 | 0.00010156 | 9.3004e-05 | 8.544e-05 | 7.8725e-05 | 7.2742e-05 | 6.7389e-05 | 6.2584e-05 | 5.8257e-05 | 5.4348e-05 | 5.0806e-05 | 4.7588e-05 | 4.4656e-05 | 4.1978e-05 | 3.9527e-05 | 3.7279e-05 | 3.5211e-05 | 3.3306e-05 | 3.1547e-05 | 2.992e-05 | 2.8413e-05 | 2.7014e-05 | 2.5713e-05 | 2.4502e-05 | 2.3373e-05 | 2.2318e-05 | 2.1332e-05 | 2.0408e-05 | 1.9542e-05 | 1.8729e-05 | 1.7965e-05 | 1.7246e-05 | 1.6568e-05 | 1.5929e-05 | 1.5326e-05 | 1.4756e-05 | 1.4217e-05 | 1.3706e-05 | 1.3222e-05 | 1.2763e-05 | 1.2327e-05 | 1.1913e-05 | 1.1519e-05 | 1.1145e-05 | 1.0788e-05 | 1.0448e-05 | 1.0123e-05 | 9.8136e-06 | 9.5179e-06 | 9.2353e-06 | 8.965e-06 | 8.7063e-06 | 8.4587e-06 | 8.2214e-06 | 7.994e-06 | 7.7758e-06 | 7.5664e-06 | 7.3654e-06 | 7.1723e-06 | 6.9866e-06 | 6.8081e-06 | 6.6364e-06 | 6.471e-06 | 6.3118e-06 | 6.1584e-06 | 6.0106e-06 | 5.868e-06 | 5.7304e-06 | 5.5977e-06 | 5.4695e-06 | 5.3457e-06 | 5.2261e-06 | 5.1104e-06 | 4.9986e-06 | 0.013689
3000 | 1.7529 | 0.21423 | 0.063722 | 0.027186 | 0.014118 | 0.0082981 | 0.0053112 | 0.0036176 | 0.0025836 | 0.0019153 | 0.0014633 | 0.001146 | 0.00091638 | 0.00074583 | 0.00061632 | 0.00051607 | 0.00043716 | 0.00037412 | 0.00032311 | 0.00028133 | 0.00024676 | 0.00021788 | 0.00019355 | 0.00017288 | 0.00015521 | 0.00013998 | 0.0001268 | 0.00011531 | 0.00010525 | 9.6397e-05 | 8.857e-05 | 8.1622e-05 | 7.5429e-05 | 6.9888e-05 | 6.4914e-05 | 6.0434e-05 | 5.6386e-05 | 5.2718e-05 | 4.9385e-05 | 4.6348e-05 | 4.3575e-05 | 4.1035e-05 | 3.8705e-05 | 3.6562e-05 | 3.4588e-05 | 3.2765e-05 | 3.1079e-05 | 2.9516e-05 | 2.8066e-05 | 2.6718e-05 | 2.5462e-05 | 2.4291e-05 | 2.3197e-05 | 2.2174e-05 | 2.1216e-05 | 2.0317e-05 | 1.9474e-05 | 1.8681e-05 | 1.7935e-05 | 1.7232e-05 | 1.6568e-05 | 1.5942e-05 | 1.535e-05 | 1.4791e-05 | 1.4261e-05 | 1.3758e-05 | 1.3281e-05 | 1.2829e-05 | 1.2399e-05 | 1.199e-05 | 1.1601e-05 | 1.123e-05 | 1.0877e-05 | 1.054e-05 | 1.0218e-05 | 9.9108e-06 | 9.6172e-06 | 9.3363e-06 | 9.0675e-06 | 8.8102e-06 | 8.5636e-06 | 8.3272e-06 | 8.1004e-06 | 7.8828e-06 | 7.6738e-06 | 7.473e-06 | 7.28e-06 | 7.0944e-06 | 6.9158e-06 | 6.7439e-06 | 6.5783e-06 | 6.4188e-06 | 6.265e-06 | 6.1167e-06 | 5.9737e-06 | 5.8356e-06 | 5.7022e-06 | 5.5734e-06 | 5.449e-06 | 5.3287e-06 | 5.2123e-06 | 0.014118
2950 | 1.8083 | 0.22095 | 0.065727 | 0.028047 | 0.014568 | 0.0085648 | 0.0054832 | 0.0037357 | 0.0026686 | 0.0019788 | 0.0015121 | 0.0011846 | 0.00094743 | 0.00077128 | 0.00063749 | 0.00053391 | 0.00045237 | 0.00038722 | 0.00033448 | 0.00029129 | 0.00025555 | 0.00022568 | 0.00020051 | 0.00017914 | 0.00016085 | 0.0001451 | 0.00013145 | 0.00011956 | 0.00010915 | 9.9983e-05 | 9.1879e-05 | 8.4683e-05 | 7.8269e-05 | 7.2531e-05 | 6.7378e-05 | 6.2736e-05 | 5.8542e-05 | 5.4741e-05 | 5.1287e-05 | 4.8139e-05 | 4.5264e-05 | 4.2631e-05 | 4.0215e-05 | 3.7993e-05 | 3.5946e-05 | 3.4055e-05 | 3.2306e-05 | 3.0685e-05 | 2.9181e-05 | 2.7781e-05 | 2.6478e-05 | 2.5263e-05 | 2.4128e-05 | 2.3066e-05 | 2.2072e-05 | 2.1139e-05 | 2.0263e-05 | 1.944e-05 | 1.8665e-05 | 1.7935e-05 | 1.7246e-05 | 1.6596e-05 | 1.5981e-05 | 1.5399e-05 | 1.4849e-05 | 1.4327e-05 | 1.3831e-05 | 1.3361e-05 | 1.2914e-05 | 1.2489e-05 | 1.2085e-05 | 1.1699e-05 | 1.1332e-05 | 1.0982e-05 | 1.0647e-05 | 1.0328e-05 | 1.0023e-05 | 9.7305e-06 | 9.451e-06 | 9.1833e-06 | 8.9269e-06 | 8.681e-06 | 8.4451e-06 | 8.2187e-06 | 8.0013e-06 | 7.7924e-06 | 7.5916e-06 | 7.3985e-06 | 7.2127e-06 | 7.0338e-06 | 6.8614e-06 | 6.6954e-06 | 6.5354e-06 | 6.381e-06 | 6.2321e-06 | 6.0883e-06 | 5.9495e-06 | 5.8154e-06 | 5.6859e-06 | 5.5606e-06 | 5.4395e-06 | 0.014568
2900 | 1.8664 | 0.228 | 0.067833 | 0.028951 | 0.015041 | 0.0088452 | 0.0056642 | 0.00386 | 0.0027581 | 0.0020456 | 0.0015636 | 0.0012252 | 0.00098015 | 0.0007981 | 0.0006598 | 0.00055272 | 0.00046841 | 0.00040103 | 0.00034648 | 0.0003018 | 0.00026482 | 0.00023392 | 0.00020787 | 0.00018574 | 0.00016681 | 0.0001505 | 0.00013637 | 0.00012406 | 0.00011327 | 0.00010377 | 9.5378e-05 | 8.7922e-05 | 8.1275e-05 | 7.5327e-05 | 6.9986e-05 | 6.5173e-05 | 6.0825e-05 | 5.6883e-05 | 5.33e-05 | 5.0036e-05 | 4.7053e-05 | 4.4322e-05 | 4.1815e-05 | 3.951e-05 | 3.7385e-05 | 3.5422e-05 | 3.3607e-05 | 3.1924e-05 | 3.0362e-05 | 2.8909e-05 | 2.7556e-05 | 2.6294e-05 | 2.5115e-05 | 2.4012e-05 | 2.2979e-05 | 2.201e-05 | 2.11e-05 | 2.0245e-05 | 1.944e-05 | 1.8681e-05 | 1.7965e-05 | 1.7289e-05 | 1.665e-05 | 1.6046e-05 | 1.5473e-05 | 1.493e-05 | 1.4415e-05 | 1.3926e-05 | 1.3462e-05 | 1.302e-05 | 1.2599e-05 | 1.2198e-05 | 1.1816e-05 | 1.1451e-05 | 1.1103e-05 | 1.0771e-05 | 1.0453e-05 | 1.0149e-05 | 9.8585e-06 | 9.58e-06 | 9.313e-06 | 9.0571e-06 | 8.8115e-06 | 8.5759e-06 | 8.3495e-06 | 8.132e-06 | 7.9229e-06 | 7.7218e-06 | 7.5283e-06 | 7.342e-06 | 7.1625e-06 | 6.9896e-06 | 6.8229e-06 | 6.6621e-06 | 6.5069e-06 | 6.3572e-06 | 6.2126e-06 | 6.0729e-06 | 5.9379e-06 | 5.8074e-06 | 5.6811e-06 | 0.015041
2850 | 1.9275 | 0.23542 | 0.070047 | 0.029902 | 0.015539 | 0.0091403 | 0.0058547 | 0.0039908 | 0.0028523 | 0.0021161 | 0.0016179 | 0.001268 | 0.0010147 | 0.00082639 | 0.00068335 | 0.00057258 | 0.00048534 | 0.00041562 | 0.00035916 | 0.00031291 | 0.00027462 | 0.00024262 | 0.00021565 | 0.00019273 | 0.00017311 | 0.00015622 | 0.00014158 | 0.00012881 | 0.00011763 | 0.00010779 | 9.9084e-05 | 9.1352e-05 | 8.4459e-05 | 7.8289e-05 | 7.2749e-05 | 6.7756e-05 | 6.3244e-05 | 5.9153e-05 | 5.5435e-05 | 5.2047e-05 | 4.8951e-05 | 4.6115e-05 | 4.3512e-05 | 4.1118e-05 | 3.8911e-05 | 3.6873e-05 | 3.4987e-05 | 3.3239e-05 | 3.1616e-05 | 3.0107e-05 | 2.8701e-05 | 2.7389e-05 | 2.6164e-05 | 2.5017e-05 | 2.3943e-05 | 2.2936e-05 | 2.199e-05 | 2.11e-05 | 2.0263e-05 | 1.9474e-05 | 1.8729e-05 | 1.8026e-05 | 1.7362e-05 | 1.6733e-05 | 1.6137e-05 | 1.5572e-05 | 1.5036e-05 | 1.4527e-05 | 1.4044e-05 | 1.3583e-05 | 1.3145e-05 | 1.2728e-05 | 1.233e-05 | 1.1951e-05 | 1.1589e-05 | 1.1243e-05 | 1.0912e-05 | 1.0595e-05 | 1.0292e-05 | 1.0002e-05 | 9.7239e-06 | 9.4573e-06 | 9.2015e-06 | 8.9559e-06 | 8.7201e-06 | 8.4935e-06 | 8.2756e-06 | 8.066e-06 | 7.8643e-06 | 7.6701e-06 | 7.4831e-06 | 7.3028e-06 | 7.129e-06 | 6.9614e-06 | 6.7996e-06 | 6.6435e-06 | 6.4927e-06 | 6.3471e-06 | 6.2063e-06 | 6.0702e-06 | 5.9385e-06 | 0.015539
2800 | 1.9918 | 0.24322 | 0.072376 | 0.030903 | 0.016063 | 0.009451 | 0.0060553 | 0.0041287 | 0.0029517 | 0.0021904 | 0.0016751 | 0.0013132 | 0.0010511 | 0.00085627 | 0.00070823 | 0.00059356 | 0.00050324 | 0.00043104 | 0.00037257 | 0.00032466 | 0.000285 | 0.00025184 | 0.00022388 | 0.00020012 | 0.00017979 | 0.00016227 | 0.00014709 | 0.00013385 | 0.00012226 | 0.00011204 | 0.00010301 | 9.4989e-05 | 8.7835e-05 | 8.1431e-05 | 7.568e-05 | 7.0496e-05 | 6.5811e-05 | 6.1563e-05 | 5.7701e-05 | 5.4181e-05 | 5.0965e-05 | 4.8019e-05 | 4.5315e-05 | 4.2827e-05 | 4.0533e-05 | 3.8415e-05 | 3.6454e-05 | 3.4637e-05 | 3.2949e-05 | 3.138e-05 | 2.9917e-05 | 2.8553e-05 | 2.7279e-05 | 2.6086e-05 | 2.4969e-05 | 2.3921e-05 | 2.2936e-05 | 2.201e-05 | 2.1139e-05 | 2.0317e-05 | 1.9542e-05 | 1.881e-05 | 1.8118e-05 | 1.7463e-05 | 1.6843e-05 | 1.6255e-05 | 1.5697e-05 | 1.5167e-05 | 1.4663e-05 | 1.4184e-05 | 1.3728e-05 | 1.3293e-05 | 1.2878e-05 | 1.2483e-05 | 1.2105e-05 | 1.1745e-05 | 1.14e-05 | 1.107e-05 | 1.0754e-05 | 1.0452e-05 | 1.0162e-05 | 9.8837e-06 | 9.617e-06 | 9.3609e-06 | 9.115e-06 | 8.8786e-06 | 8.6514e-06 | 8.4328e-06 | 8.2224e-06 | 8.0199e-06 | 7.8247e-06 | 7.6367e-06 | 7.4554e-06 | 7.2805e-06 | 7.1117e-06 | 6.9488e-06 | 6.7914e-06 | 6.6394e-06 | 6.4925e-06 | 6.3504e-06 | 6.213e-06 | 0.016063
2750 | 2.0595 | 0.25143 | 0.074829 | 0.031957 | 0.016615 | 0.0097786 | 0.006267 | 0.0042742 | 0.0030566 | 0.0022688 | 0.0017356 | 0.0013609 | 0.0010896 | 0.00088786 | 0.00073454 | 0.00061575 | 0.00052218 | 0.00044736 | 0.00038677 | 0.00033711 | 0.00029598 | 0.0002616 | 0.0002326 | 0.00020796 | 0.00018687 | 0.00016869 | 0.00015294 | 0.0001392 | 0.00012716 | 0.00011656 | 0.00010718 | 9.885e-05 | 9.1419e-05 | 8.4768e-05 | 7.8792e-05 | 7.3407e-05 | 6.8538e-05 | 6.4123e-05 | 6.0109e-05 | 5.645e-05 | 5.3106e-05 | 5.0043e-05 | 4.7231e-05 | 4.4643e-05 | 4.2258e-05 | 4.0054e-05 | 3.8014e-05 | 3.6124e-05 | 3.4367e-05 | 3.2734e-05 | 3.1212e-05 | 2.9792e-05 | 2.8465e-05 | 2.7224e-05 | 2.606e-05 | 2.4969e-05 | 2.3943e-05 | 2.2979e-05 | 2.2072e-05 | 2.1216e-05 | 2.0408e-05 | 1.9646e-05 | 1.8925e-05 | 1.8242e-05 | 1.7596e-05 | 1.6983e-05 | 1.6401e-05 | 1.5849e-05 | 1.5323e-05 | 1.4824e-05 | 1.4348e-05 | 1.3895e-05 | 1.3462e-05 | 1.305e-05 | 1.2656e-05 | 1.228e-05 | 1.192e-05 | 1.1576e-05 | 1.1247e-05 | 1.0931e-05 | 1.0629e-05 | 1.0339e-05 | 1.006e-05 | 9.793e-06 | 9.5363e-06 | 9.2896e-06 | 9.0524e-06 | 8.8242e-06 | 8.6046e-06 | 8.3931e-06 | 8.1894e-06 | 7.993e-06 | 7.8037e-06 | 7.621e-06 | 7.4448e-06 | 7.2746e-06 | 7.1103e-06 | 6.9515e-06 | 6.798e-06 | 6.6496e-06 | 6.506e-06 | 0.016615
2700 | 2.1309 | 0.26009 | 0.077415 | 0.033069 | 0.017198 | 0.010124 | 0.0064904 | 0.0044279 | 0.0031674 | 0.0023517 | 0.0017995 | 0.0014114 | 0.0011303 | 0.00092128 | 0.00076238 | 0.00063926 | 0.00054224 | 0.00046466 | 0.00040181 | 0.0003503 | 0.00030763 | 0.00027195 | 0.00024186 | 0.00021628 | 0.00019438 | 0.00017551 | 0.00015915 | 0.00014488 | 0.00013237 | 0.00012136 | 0.00011161 | 0.00010295 | 9.5229e-05 | 8.8314e-05 | 8.2102e-05 | 7.6502e-05 | 7.1438e-05 | 6.6847e-05 | 6.2671e-05 | 5.8865e-05 | 5.5385e-05 | 5.2197e-05 | 4.9271e-05 | 4.6577e-05 | 4.4094e-05 | 4.1799e-05 | 3.9676e-05 | 3.7707e-05 | 3.5878e-05 | 3.4177e-05 | 3.2591e-05 | 3.1112e-05 | 2.973e-05 | 2.8436e-05 | 2.7224e-05 | 2.6086e-05 | 2.5017e-05 | 2.4012e-05 | 2.3066e-05 | 2.2174e-05 | 2.1332e-05 | 2.0537e-05 | 1.9785e-05 | 1.9073e-05 | 1.8399e-05 | 1.7759e-05 | 1.7152e-05 | 1.6576e-05 | 1.6028e-05 | 1.5507e-05 | 1.501e-05 | 1.4537e-05 | 1.4086e-05 | 1.3656e-05 | 1.3244e-05 | 1.2852e-05 | 1.2476e-05 | 1.2117e-05 | 1.1773e-05 | 1.1443e-05 | 1.1127e-05 | 1.0824e-05 | 1.0534e-05 | 1.0254e-05 | 9.9864e-06 | 9.7286e-06 | 9.4808e-06 | 9.2424e-06 | 9.0129e-06 | 8.7919e-06 | 8.579e-06 | 8.3738e-06 | 8.1759e-06 | 7.985e-06 | 7.8008e-06 | 7.6229e-06 | 7.4511e-06 | 7.2851e-06 | 7.1246e-06 | 6.9694e-06 | 6.8193e-06 | 0.017198
2650 | 2.2062 | 0.26922 | 0.080143 | 0.034242 | 0.017813 | 0.01049 | 0.0067265 | 0.0045903 | 0.0032845 | 0.0024394 | 0.0018671 | 0.0014649 | 0.0011735 | 0.0009567 | 0.0007919 | 0.00066417 | 0.00056351 | 0.00048301 | 0.00041777 | 0.0003643 | 0.00031999 | 0.00028294 | 0.00025169 | 0.00022512 | 0.00020237 | 0.00018275 | 0.00016575 | 0.00015092 | 0.00013791 | 0.00012646 | 0.00011632 | 0.00010732 | 9.9284e-05 | 9.209e-05 | 8.5625e-05 | 7.9797e-05 | 7.4527e-05 | 6.9747e-05 | 6.54e-05 | 6.1437e-05 | 5.7813e-05 | 5.4493e-05 | 5.1445e-05 | 4.8639e-05 | 4.6051e-05 | 4.3661e-05 | 4.1448e-05 | 3.9396e-05 | 3.7489e-05 | 3.5716e-05 | 3.4063e-05 | 3.252e-05 | 3.1079e-05 | 2.973e-05 | 2.8465e-05 | 2.7279e-05 | 2.6164e-05 | 2.5115e-05 | 2.4128e-05 | 2.3197e-05 | 2.2318e-05 | 2.1488e-05 | 2.0703e-05 | 1.996e-05 | 1.9256e-05 | 1.8589e-05 | 1.7955e-05 | 1.7353e-05 | 1.6781e-05 | 1.6236e-05 | 1.5718e-05 | 1.5224e-05 | 1.4752e-05 | 1.4303e-05 | 1.3873e-05 | 1.3463e-05 | 1.307e-05 | 1.2695e-05 | 1.2335e-05 | 1.1991e-05 | 1.1661e-05 | 1.1344e-05 | 1.104e-05 | 1.0748e-05 | 1.0468e-05 | 1.0198e-05 | 9.9391e-06 | 9.6898e-06 | 9.4498e-06 | 9.2186e-06 | 8.9959e-06 | 8.7813e-06 | 8.5743e-06 | 8.3745e-06 | 8.1818e-06 | 7.9957e-06 | 7.8159e-06 | 7.6422e-06 | 7.4742e-06 | 7.3118e-06 | 7.1547e-06 | 0.017813
2600 | 2.2858 | 0.27887 | 0.083026 | 0.035482 | 0.018464 | 0.010876 | 0.0069764 | 0.0047623 | 0.0034086 | 0.0025324 | 0.0019388 | 0.0015216 | 0.0012192 | 0.00099427 | 0.00082322 | 0.00069062 | 0.0005861 | 0.00050249 | 0.00043473 | 0.00037917 | 0.00033314 | 0.00029463 | 0.00026214 | 0.00023452 | 0.00021086 | 0.00019046 | 0.00017277 | 0.00015734 | 0.00014381 | 0.00013189 | 0.00012135 | 0.00011197 | 0.00010361 | 9.6114e-05 | 8.9381e-05 | 8.3311e-05 | 7.7821e-05 | 7.2841e-05 | 6.8311e-05 | 6.418e-05 | 6.0404e-05 | 5.6943e-05 | 5.3765e-05 | 5.0839e-05 | 4.8141e-05 | 4.5648e-05 | 4.334e-05 | 4.1199e-05 | 3.921e-05 | 3.736e-05 | 3.5635e-05 | 3.4025e-05 | 3.252e-05 | 3.1112e-05 | 2.9792e-05 | 2.8553e-05 | 2.7389e-05 | 2.6294e-05 | 2.5263e-05 | 2.4291e-05 | 2.3373e-05 | 2.2506e-05 | 2.1686e-05 | 2.091e-05 | 2.0174e-05 | 1.9476e-05 | 1.8814e-05 | 1.8185e-05 | 1.7587e-05 | 1.7017e-05 | 1.6475e-05 | 1.5959e-05 | 1.5466e-05 | 1.4995e-05 | 1.4546e-05 | 1.4117e-05 | 1.3706e-05 | 1.3314e-05 | 1.2938e-05 | 1.2577e-05 | 1.2232e-05 | 1.19e-05 | 1.1582e-05 | 1.1277e-05 | 1.0983e-05 | 1.0701e-05 | 1.043e-05 | 1.0169e-05 | 9.9178e-06 | 9.6758e-06 | 9.4426e-06 | 9.2178e-06 | 9.0011e-06 | 8.7919e-06 | 8.5901e-06 | 8.3951e-06 | 8.2068e-06 | 8.0249e-06 | 7.8489e-06 | 7.6788e-06 | 7.5142e-06 | 0.018464
2550 | 2.3699 | 0.28907 | 0.086074 | 0.036794 | 0.019152 | 0.011285 | 0.007241 | 0.0049445 | 0.0035402 | 0.0026309 | 0.0020149 | 0.0015818 | 0.0012678 | 0.0010342 | 0.00085649 | 0.00071873 | 0.00061011 | 0.00052321 | 0.00045277 | 0.000395 | 0.00034713 | 0.00030707 | 0.00027327 | 0.00024453 | 0.00021991 | 0.00019868 | 0.00018026 | 0.00016419 | 0.0001501 | 0.00013769 | 0.0001267 | 0.00011693 | 0.00010822 | 0.00010041 | 9.339e-05 | 8.7062e-05 | 8.1337e-05 | 7.6144e-05 | 7.142e-05 | 6.7111e-05 | 6.3172e-05 | 5.9561e-05 | 5.6244e-05 | 5.3191e-05 | 5.0375e-05 | 4.7772e-05 | 4.5363e-05 | 4.3127e-05 | 4.1051e-05 | 3.9118e-05 | 3.7317e-05 | 3.5635e-05 | 3.4063e-05 | 3.2591e-05 | 3.1212e-05 | 2.9917e-05 | 2.8701e-05 | 2.7556e-05 | 2.6478e-05 | 2.5462e-05 | 2.4502e-05 | 2.3596e-05 | 2.2738e-05 | 2.1926e-05 | 2.1157e-05 | 2.0427e-05 | 1.9734e-05 | 1.9076e-05 | 1.845e-05 | 1.7854e-05 | 1.7287e-05 | 1.6746e-05 | 1.623e-05 | 1.5738e-05 | 1.5268e-05 | 1.4818e-05 | 1.4389e-05 | 1.3977e-05 | 1.3583e-05 | 1.3206e-05 | 1.2844e-05 | 1.2497e-05 | 1.2164e-05 | 1.1844e-05 | 1.1536e-05 | 1.1241e-05 | 1.0957e-05 | 1.0683e-05 | 1.042e-05 | 1.0166e-05 | 9.9219e-06 | 9.6863e-06 | 9.4591e-06 | 9.2398e-06 | 9.0282e-06 | 8.8239e-06 | 8.6264e-06 | 8.4356e-06 | 8.2512e-06 | 8.0728e-06 | 7.9002e-06 | 0.019152
2500 | 2.4589 | 0.29986 | 0.089301 | 0.038184 | 0.019881 | 0.011718 | 0.0075217 | 0.0051379 | 0.0036798 | 0.0027355 | 0.0020957 | 0.0016457 | 0.0013194 | 0.0010766 | 0.00089189 | 0.00074864 | 0.00063567 | 0.00054528 | 0.00047199 | 0.00041187 | 0.00036203 | 0.00032034 | 0.00028514 | 0.00025521 | 0.00022956 | 0.00020744 | 0.00018825 | 0.00017151 | 0.00015682 | 0.00014388 | 0.00013242 | 0.00012223 | 0.00011314 | 0.000105 | 9.7675e-05 | 9.1072e-05 | 8.5098e-05 | 7.9677e-05 | 7.4746e-05 | 7.0247e-05 | 6.6133e-05 | 6.2362e-05 | 5.8898e-05 | 5.5709e-05 | 5.2766e-05 | 5.0047e-05 | 4.7529e-05 | 4.5193e-05 | 4.3022e-05 | 4.1001e-05 | 3.9118e-05 | 3.736e-05 | 3.5716e-05 | 3.4177e-05 | 3.2734e-05 | 3.138e-05 | 3.0107e-05 | 2.8909e-05 | 2.7781e-05 | 2.6718e-05 | 2.5713e-05 | 2.4764e-05 | 2.3867e-05 | 2.3017e-05 | 2.2211e-05 | 2.1447e-05 | 2.0721e-05 | 2.0032e-05 | 1.9376e-05 | 1.8752e-05 | 1.8158e-05 | 1.7591e-05 | 1.7051e-05 | 1.6535e-05 | 1.6042e-05 | 1.5571e-05 | 1.5121e-05 | 1.469e-05 | 1.4277e-05 | 1.3881e-05 | 1.3502e-05 | 1.3138e-05 | 1.2788e-05 | 1.2453e-05 | 1.2131e-05 | 1.1821e-05 | 1.1522e-05 | 1.1236e-05 | 1.0959e-05 | 1.0693e-05 | 1.0437e-05 | 1.019e-05 | 9.9513e-06 | 9.7212e-06 | 9.4991e-06 | 9.2846e-06 | 9.0774e-06 | 8.8772e-06 | 8.6835e-06 | 8.4962e-06 | 8.315e-06 | 0.019881
2450 | 2.5533 | 0.3113 | 0.092721 | 0.039657 | 0.020655 | 0.012178 | 0.0078197 | 0.0053433 | 0.0038282 | 0.0028468 | 0.0021816 | 0.0017137 | 0.0013744 | 0.0011218 | 0.0009296 | 0.00078051 | 0.00066292 | 0.0005688 | 0.00049248 | 0.00042986 | 0.00037794 | 0.00033449 | 0.00029782 | 0.00026661 | 0.00023987 | 0.00021681 | 0.00019679 | 0.00017933 | 0.000164 | 0.0001505 | 0.00013854 | 0.00012791 | 0.00011841 | 0.00010991 | 0.00010226 | 9.5365e-05 | 8.9124e-05 | 8.3461e-05 | 7.8308e-05 | 7.3606e-05 | 6.9306e-05 | 6.5364e-05 | 6.1742e-05 | 5.8407e-05 | 5.533e-05 | 5.2486e-05 | 4.9851e-05 | 4.7407e-05 | 4.5136e-05 | 4.3022e-05 | 4.1051e-05 | 3.921e-05 | 3.7489e-05 | 3.5878e-05 | 3.4367e-05 | 3.2949e-05 | 3.1616e-05 | 3.0362e-05 | 2.9181e-05 | 2.8066e-05 | 2.7014e-05 | 2.6019e-05 | 2.5079e-05 | 2.4188e-05 | 2.3343e-05 | 2.2542e-05 | 2.1782e-05 | 2.1059e-05 | 2.0372e-05 | 1.9717e-05 | 1.9094e-05 | 1.85e-05 | 1.7933e-05 | 1.7392e-05 | 1.6875e-05 | 1.6381e-05 | 1.5908e-05 | 1.5456e-05 | 1.5022e-05 | 1.4607e-05 | 1.4209e-05 | 1.3827e-05 | 1.346e-05 | 1.3108e-05 | 1.277e-05 | 1.2444e-05 | 1.2131e-05 | 1.183e-05 | 1.154e-05 | 1.126e-05 | 1.0991e-05 | 1.0731e-05 | 1.0481e-05 | 1.0239e-05 | 1.0006e-05 | 9.7807e-06 | 9.5629e-06 | 9.3525e-06 | 9.149e-06 | 8.9522e-06 | 8.7618e-06 | 0.020655
2400 | 2.6535 | 0.32344 | 0.096352 | 0.041222 | 0.021477 | 0.012667 | 0.0081366 | 0.0055617 | 0.0039861 | 0.0029653 | 0.0022731 | 0.0017862 | 0.001433 | 0.00117 | 0.00096982 | 0.00081452 | 0.00069201 | 0.00059393 | 0.00051437 | 0.00044908 | 0.00039495 | 0.00034963 | 0.00031137 | 0.00027881 | 0.0002509 | 0.00022683 | 0.00020593 | 0.0001877 | 0.00017169 | 0.00015759 | 0.00014509 | 0.00013398 | 0.00012406 | 0.00011517 | 0.00010718 | 9.9969e-05 | 9.3443e-05 | 8.752e-05 | 8.2129e-05 | 7.721e-05 | 7.2711e-05 | 6.8586e-05 | 6.4795e-05 | 6.1304e-05 | 5.8083e-05 | 5.5105e-05 | 5.2346e-05 | 4.9786e-05 | 4.7407e-05 | 4.5193e-05 | 4.3127e-05 | 4.1199e-05 | 3.9396e-05 | 3.7707e-05 | 3.6124e-05 | 3.4637e-05 | 3.3239e-05 | 3.1924e-05 | 3.0685e-05 | 2.9516e-05 | 2.8413e-05 | 2.737e-05 | 2.6383e-05 | 2.5448e-05 | 2.4562e-05 | 2.3722e-05 | 2.2923e-05 | 2.2165e-05 | 2.1443e-05 | 2.0756e-05 | 2.0102e-05 | 1.9478e-05 | 1.8883e-05 | 1.8315e-05 | 1.7772e-05 | 1.7253e-05 | 1.6756e-05 | 1.6281e-05 | 1.5826e-05 | 1.5389e-05 | 1.4971e-05 | 1.457e-05 | 1.4184e-05 | 1.3814e-05 | 1.3458e-05 | 1.3116e-05 | 1.2787e-05 | 1.2471e-05 | 1.2166e-05 | 1.1872e-05 | 1.1589e-05 | 1.1316e-05 | 1.1052e-05 | 1.0798e-05 | 1.0553e-05 | 1.0315e-05 | 1.0086e-05 | 9.8651e-06 | 9.651e-06 | 9.4439e-06 | 9.2435e-06 | 0.021477
2350 | 2.7599 | 0.33633 | 0.10021 | 0.042885 | 0.022351 | 0.013188 | 0.008474 | 0.0057945 | 0.0041544 | 0.0030916 | 0.0023708 | 0.0018636 | 0.0014955 | 0.0012215 | 0.0010128 | 0.00085087 | 0.0007231 | 0.00062079 | 0.00053779 | 0.00046966 | 0.00041315 | 0.00036584 | 0.00032588 | 0.00029188 | 0.00026272 | 0.00023757 | 0.00021573 | 0.00019667 | 0.00017994 | 0.00016519 | 0.00015213 | 0.00014051 | 0.00013013 | 0.00012083 | 0.00011246 | 0.00010491 | 9.8081e-05 | 9.188e-05 | 8.6235e-05 | 8.1084e-05 | 7.6371e-05 | 7.2049e-05 | 6.8077e-05 | 6.4419e-05 | 6.1043e-05 | 5.7922e-05 | 5.503e-05 | 5.2346e-05 | 4.9851e-05 | 4.7529e-05 | 4.5363e-05 | 4.334e-05 | 4.1448e-05 | 3.9676e-05 | 3.8014e-05 | 3.6454e-05 | 3.4987e-05 | 3.3607e-05 | 3.2306e-05 | 3.1079e-05 | 2.992e-05 | 2.8825e-05 | 2.7788e-05 | 2.6806e-05 | 2.5876e-05 | 2.4993e-05 | 2.4154e-05 | 2.3357e-05 | 2.2598e-05 | 2.1876e-05 | 2.1189e-05 | 2.0533e-05 | 1.9907e-05 | 1.931e-05 | 1.8739e-05 | 1.8193e-05 | 1.7671e-05 | 1.7171e-05 | 1.6692e-05 | 1.6233e-05 | 1.5793e-05 | 1.5371e-05 | 1.4966e-05 | 1.4576e-05 | 1.4202e-05 | 1.3842e-05 | 1.3495e-05 | 1.3162e-05 | 1.2841e-05 | 1.2532e-05 | 1.2234e-05 | 1.1946e-05 | 1.1669e-05 | 1.1401e-05 | 1.1143e-05 | 1.0893e-05 | 1.0652e-05 | 1.0419e-05 | 1.0193e-05 | 9.975e-06 | 9.7639e-06 | 0.022351
2300 | 2.8731 | 0.35005 | 0.10432 | 0.044656 | 0.023282 | 0.013742 | 0.0088337 | 0.0060428 | 0.004334 | 0.0032264 | 0.0024751 | 0.0019462 | 0.0015624 | 0.0012765 | 0.0010588 | 0.00088978 | 0.0007564 | 0.00064957 | 0.00056287 | 0.0004917 | 0.00043266 | 0.00038322 | 0.00034145 | 0.0003059 | 0.00027541 | 0.0002491 | 0.00022626 | 0.00020631 | 0.0001888 | 0.00017336 | 0.00015968 | 0.00014752 | 0.00013665 | 0.0001269 | 0.00011814 | 0.00011023 | 0.00010307 | 9.6572e-05 | 9.0655e-05 | 8.5254e-05 | 8.0312e-05 | 7.5779e-05 | 7.1613e-05 | 6.7775e-05 | 6.4233e-05 | 6.0957e-05 | 5.7922e-05 | 5.5105e-05 | 5.2486e-05 | 5.0047e-05 | 4.7772e-05 | 4.5648e-05 | 4.3661e-05 | 4.1799e-05 | 4.0054e-05 | 3.8415e-05 | 3.6873e-05 | 3.5422e-05 | 3.4055e-05 | 3.2765e-05 | 3.1547e-05 | 3.0395e-05 | 2.9305e-05 | 2.8273e-05 | 2.7294e-05 | 2.6365e-05 | 2.5483e-05 | 2.4644e-05 | 2.3846e-05 | 2.3086e-05 | 2.2363e-05 | 2.1672e-05 | 2.1014e-05 | 2.0385e-05 | 1.9784e-05 | 1.9209e-05 | 1.866e-05 | 1.8133e-05 | 1.7629e-05 | 1.7146e-05 | 1.6682e-05 | 1.6237e-05 | 1.581e-05 | 1.54e-05 | 1.5005e-05 | 1.4626e-05 | 1.4261e-05 | 1.391e-05 | 1.3572e-05 | 1.3246e-05 | 1.2931e-05 | 1.2628e-05 | 1.2336e-05 | 1.2054e-05 | 1.1781e-05 | 1.1518e-05 | 1.1264e-05 | 1.1018e-05 | 1.078e-05 | 1.055e-05 | 1.0327e-05 | 0.023282
2250 | 2.9938 | 0.36466 | 0.10869 | 0.046544 | 0.024275 | 0.014334 | 0.0092178 | 0.006308 | 0.004526 | 0.0033706 | 0.0025867 | 0.0020347 | 0.001634 | 0.0013355 | 0.001108 | 0.00093149 | 0.00079211 | 0.00068044 | 0.0005898 | 0.00051537 | 0.00045362 | 0.00040188 | 0.00035818 | 0.00032097 | 0.00028905 | 0.0002615 | 0.00023758 | 0.00021668 | 0.00019834 | 0.00018216 | 0.00016782 | 0.00015507 | 0.00014367 | 0.00013345 | 0.00012426 | 0.00011596 | 0.00010845 | 0.00010163 | 9.542e-05 | 8.975e-05 | 8.4562e-05 | 7.9802e-05 | 7.5427e-05 | 7.1396e-05 | 6.7674e-05 | 6.4233e-05 | 6.1043e-05 | 5.8083e-05 | 5.533e-05 | 5.2766e-05 | 5.0375e-05 | 4.8141e-05 | 4.6051e-05 | 4.4094e-05 | 4.2258e-05 | 4.0533e-05 | 3.8911e-05 | 3.7385e-05 | 3.5946e-05 | 3.4588e-05 | 3.3306e-05 | 3.2093e-05 | 3.0946e-05 | 2.9858e-05 | 2.8828e-05 | 2.7849e-05 | 2.692e-05 | 2.6037e-05 | 2.5196e-05 | 2.4396e-05 | 2.3633e-05 | 2.2906e-05 | 2.2212e-05 | 2.1549e-05 | 2.0915e-05 | 2.031e-05 | 1.973e-05 | 1.9175e-05 | 1.8643e-05 | 1.8134e-05 | 1.7645e-05 | 1.7176e-05 | 1.6725e-05 | 1.6292e-05 | 1.5876e-05 | 1.5476e-05 | 1.5091e-05 | 1.472e-05 | 1.4363e-05 | 1.4019e-05 | 1.3687e-05 | 1.3367e-05 | 1.3059e-05 | 1.2761e-05 | 1.2473e-05 | 1.2195e-05 | 1.1927e-05 | 1.1667e-05 | 1.1416e-05 | 1.1173e-05 | 1.0938e-05 | 0.024275
2200 | 3.1225 | 0.38026 | 0.11336 | 0.048559 | 0.025337 | 0.014967 | 0.0096286 | 0.0065918 | 0.0047316 | 0.0035251 | 0.0027063 | 0.0021296 | 0.0017108 | 0.0013987 | 0.0011609 | 0.00097628 | 0.00083046 | 0.00071361 | 0.00061875 | 0.00054083 | 0.00047616 | 0.00042197 | 0.00037619 | 0.00033719 | 0.00030374 | 0.00027486 | 0.00024977 | 0.00022786 | 0.00020862 | 0.00019164 | 0.0001766 | 0.00016321 | 0.00015125 | 0.00014052 | 0.00013087 | 0.00012215 | 0.00011426 | 0.00010709 | 0.00010057 | 9.4608e-05 | 8.9154e-05 | 8.415e-05 | 7.9549e-05 | 7.531e-05 | 7.1396e-05 | 6.7775e-05 | 6.4419e-05 | 6.1304e-05 | 5.8407e-05 | 5.5709e-05 | 5.3191e-05 | 5.0839e-05 | 4.8639e-05 | 4.6577e-05 | 4.4643e-05 | 4.2827e-05 | 4.1118e-05 | 3.951e-05 | 3.7993e-05 | 3.6562e-05 | 3.5211e-05 | 3.3933e-05 | 3.2723e-05 | 3.1577e-05 | 3.049e-05 | 2.9458e-05 | 2.8478e-05 | 2.7546e-05 | 2.6659e-05 | 2.5815e-05 | 2.501e-05 | 2.4243e-05 | 2.351e-05 | 2.2811e-05 | 2.2142e-05 | 2.1503e-05 | 2.0891e-05 | 2.0305e-05 | 1.9744e-05 | 1.9205e-05 | 1.8689e-05 | 1.8194e-05 | 1.7718e-05 | 1.726e-05 | 1.6821e-05 | 1.6398e-05 | 1.5991e-05 | 1.5599e-05 | 1.5222e-05 | 1.4859e-05 | 1.4508e-05 | 1.417e-05 | 1.3844e-05 | 1.3529e-05 | 1.3225e-05 | 1.2931e-05 | 1.2647e-05 | 1.2372e-05 | 1.2106e-05 | 1.1849e-05 | 1.1601e-05 | 0.025337
2150 | 3.26 | 0.39692 | 0.11835 | 0.050715 | 0.026472 | 0.015644 | 0.010069 | 0.0068961 | 0.004952 | 0.0036909 | 0.0028346 | 0.0022315 | 0.0017933 | 0.0014667 | 0.0012178 | 0.0010245 | 0.00087175 | 0.00074933 | 0.00064992 | 0.00056825 | 0.00050045 | 0.00044363 | 0.0003956 | 0.00035469 | 0.00031959 | 0.00028928 | 0.00026294 | 0.00023993 | 0.00021972 | 0.00020189 | 0.00018608 | 0.00017201 | 0.00015944 | 0.00014816 | 0.00013801 | 0.00012884 | 0.00012054 | 0.000113 | 0.00010614 | 9.9866e-05 | 9.4125e-05 | 8.8857e-05 | 8.4013e-05 | 7.9549e-05 | 7.5427e-05 | 7.1613e-05 | 6.8077e-05 | 6.4795e-05 | 6.1742e-05 | 5.8898e-05 | 5.6244e-05 | 5.3765e-05 | 5.1445e-05 | 4.9271e-05 | 4.7231e-05 | 4.5315e-05 | 4.3512e-05 | 4.1815e-05 | 4.0215e-05 | 3.8705e-05 | 3.7279e-05 | 3.5929e-05 | 3.4652e-05 | 3.3442e-05 | 3.2294e-05 | 3.1205e-05 | 3.017e-05 | 2.9186e-05 | 2.8249e-05 | 2.7357e-05 | 2.6507e-05 | 2.5696e-05 | 2.4922e-05 | 2.4182e-05 | 2.3475e-05 | 2.28e-05 | 2.2153e-05 | 2.1533e-05 | 2.094e-05 | 2.037e-05 | 1.9824e-05 | 1.93e-05 | 1.8797e-05 | 1.8313e-05 | 1.7848e-05 | 1.7401e-05 | 1.697e-05 | 1.6556e-05 | 1.6157e-05 | 1.5772e-05 | 1.5401e-05 | 1.5043e-05 | 1.4697e-05 | 1.4364e-05 | 1.4042e-05 | 1.3731e-05 | 1.343e-05 | 1.3139e-05 | 1.2858e-05 | 1.2586e-05 | 1.2322e-05 | 0.026472
2100 | 3.4073 | 0.41475 | 0.1237 | 0.053025 | 0.027689 | 0.016371 | 0.010541 | 0.0072227 | 0.0051889 | 0.003869 | 0.0029727 | 0.0023411 | 0.0018822 | 0.00154 | 0.0012791 | 0.0010764 | 0.00091626 | 0.00078786 | 0.00068356 | 0.00059785 | 0.00052668 | 0.00046702 | 0.00041658 | 0.0003736 | 0.00033672 | 0.00030486 | 0.00027718 | 0.00025299 | 0.00023173 | 0.00021298 | 0.00019635 | 0.00018154 | 0.00016831 | 0.00015644 | 0.00014575 | 0.0001361 | 0.00012736 | 0.00011941 | 0.00011218 | 0.00010557 | 9.9518e-05 | 9.3965e-05 | 8.8857e-05 | 8.415e-05 | 7.9802e-05 | 7.5779e-05 | 7.2049e-05 | 6.8586e-05 | 6.5364e-05 | 6.2362e-05 | 5.9561e-05 | 5.6943e-05 | 5.4493e-05 | 5.2197e-05 | 5.0043e-05 | 4.8019e-05 | 4.6115e-05 | 4.4322e-05 | 4.2631e-05 | 4.1035e-05 | 3.9527e-05 | 3.8101e-05 | 3.6751e-05 | 3.5472e-05 | 3.4258e-05 | 3.3106e-05 | 3.2011e-05 | 3.097e-05 | 2.9979e-05 | 2.9035e-05 | 2.8135e-05 | 2.7277e-05 | 2.6458e-05 | 2.5675e-05 | 2.4927e-05 | 2.4212e-05 | 2.3527e-05 | 2.2871e-05 | 2.2242e-05 | 2.1639e-05 | 2.1061e-05 | 2.0506e-05 | 1.9973e-05 | 1.946e-05 | 1.8968e-05 | 1.8494e-05 | 1.8037e-05 | 1.7598e-05 | 1.7175e-05 | 1.6767e-05 | 1.6374e-05 | 1.5994e-05 | 1.5628e-05 | 1.5275e-05 | 1.4933e-05 | 1.4603e-05 | 1.4284e-05 | 1.3976e-05 | 1.3678e-05 | 1.3389e-05 | 1.311e-05 | 0.027689
2050 | 3.5651 | 0.43386 | 0.12943 | 0.055503 | 0.028996 | 0.017151 | 0.011049 | 0.0075741 | 0.0054438 | 0.0040609 | 0.0031214 | 0.0024593 | 0.001978 | 0.001619 | 0.0013453 | 0.0011325 | 0.00096435 | 0.00082949 | 0.00071992 | 0.00062986 | 0.00055505 | 0.00049233 | 0.00043929 | 0.00039408 | 0.00035528 | 0.00032176 | 0.00029261 | 0.00026714 | 0.00024476 | 0.00022501 | 0.00020749 | 0.00019188 | 0.00017794 | 0.00016542 | 0.00015415 | 0.00014398 | 0.00013476 | 0.00012638 | 0.00011874 | 0.00011177 | 0.00010538 | 9.9518e-05 | 9.4125e-05 | 8.9154e-05 | 8.4562e-05 | 8.0312e-05 | 7.6371e-05 | 7.2711e-05 | 6.9306e-05 | 6.6133e-05 | 6.3172e-05 | 6.0404e-05 | 5.7813e-05 | 5.5385e-05 | 5.3106e-05 | 5.0965e-05 | 4.8951e-05 | 4.7053e-05 | 4.5264e-05 | 4.3575e-05 | 4.1978e-05 | 4.0469e-05 | 3.9039e-05 | 3.7684e-05 | 3.6399e-05 | 3.5178e-05 | 3.4018e-05 | 3.2915e-05 | 3.1866e-05 | 3.0865e-05 | 2.9912e-05 | 2.9002e-05 | 2.8134e-05 | 2.7305e-05 | 2.6511e-05 | 2.5753e-05 | 2.5026e-05 | 2.4331e-05 | 2.3664e-05 | 2.3025e-05 | 2.2411e-05 | 2.1822e-05 | 2.1257e-05 | 2.0713e-05 | 2.019e-05 | 1.9687e-05 | 1.9203e-05 | 1.8737e-05 | 1.8287e-05 | 1.7854e-05 | 1.7437e-05 | 1.7034e-05 | 1.6645e-05 | 1.627e-05 | 1.5907e-05 | 1.5557e-05 | 1.5218e-05 | 1.489e-05 | 1.4574e-05 | 1.4267e-05 | 1.397e-05 | 0.028996
2000 | 3.7347 | 0.45439 | 0.13559 | 0.058167 | 0.030402 | 0.017992 | 0.011596 | 0.0079528 | 0.0057186 | 0.0042679 | 0.003282 | 0.0025869 | 0.0020815 | 0.0017044 | 0.0014168 | 0.0011932 | 0.0010164 | 0.00087458 | 0.00075932 | 0.00066456 | 0.00058582 | 0.00051978 | 0.00046393 | 0.00041631 | 0.00037543 | 0.0003401 | 0.00030938 | 0.00028252 | 0.00025892 | 0.00023808 | 0.0002196 | 0.00020313 | 0.00018841 | 0.0001752 | 0.0001633 | 0.00015255 | 0.00014281 | 0.00013396 | 0.00012589 | 0.00011852 | 0.00011177 | 0.00010557 | 9.9866e-05 | 9.4608e-05 | 8.975e-05 | 8.5254e-05 | 8.1084e-05 | 7.721e-05 | 7.3606e-05 | 7.0247e-05 | 6.7111e-05 | 6.418e-05 | 6.1437e-05 | 5.8865e-05 | 5.645e-05 | 5.4181e-05 | 5.2047e-05 | 5.0036e-05 | 4.8139e-05 | 4.6348e-05 | 4.4656e-05 | 4.3055e-05 | 4.1539e-05 | 4.0102e-05 | 3.8738e-05 | 3.7443e-05 | 3.6213e-05 | 3.5043e-05 | 3.3928e-05 | 3.2867e-05 | 3.1855e-05 | 3.0889e-05 | 2.9967e-05 | 2.9086e-05 | 2.8244e-05 | 2.7438e-05 | 2.6667e-05 | 2.5928e-05 | 2.522e-05 | 2.4541e-05 | 2.3889e-05 | 2.3263e-05 | 2.2662e-05 | 2.2084e-05 | 2.1528e-05 | 2.0993e-05 | 2.0479e-05 | 1.9983e-05 | 1.9505e-05 | 1.9045e-05 | 1.8601e-05 | 1.8172e-05 | 1.7759e-05 | 1.7359e-05 | 1.6974e-05 | 1.6601e-05 | 1.6241e-05 | 1.5892e-05 | 1.5555e-05 | 1.5228e-05 | 1.4912e-05 | 0.030402
1950 | 3.9171 | 0.47648 | 0.14222 | 0.061037 | 0.031917 | 0.018898 | 0.012186 | 0.0083618 | 0.0060157 | 0.0044917 | 0.0034558 | 0.0027251 | 0.0021936 | 0.001797 | 0.0014944 | 0.001259 | 0.0010729 | 0.00092353 | 0.0008021 | 0.00070224 | 0.00061925 | 0.00054963 | 0.00049072 | 0.00044049 | 0.00039735 | 0.00036006 | 0.00032763 | 0.00029927 | 0.00027434 | 0.00025233 | 0.00023279 | 0.00021539 | 0.00019983 | 0.00018586 | 0.00017328 | 0.00016191 | 0.0001516 | 0.00014223 | 0.00013369 | 0.00012589 | 0.00011874 | 0.00011218 | 0.00010614 | 0.00010057 | 9.542e-05 | 9.0655e-05 | 8.6235e-05 | 8.2129e-05 | 7.8308e-05 | 7.4746e-05 | 7.142e-05 | 6.8311e-05 | 6.54e-05 | 6.2671e-05 | 6.0109e-05 | 5.7701e-05 | 5.5435e-05 | 5.33e-05 | 5.1287e-05 | 4.9385e-05 | 4.7588e-05 | 4.5887e-05 | 4.4277e-05 | 4.275e-05 | 4.1301e-05 | 3.9925e-05 | 3.8617e-05 | 3.7373e-05 | 3.6189e-05 | 3.506e-05 | 3.3984e-05 | 3.2957e-05 | 3.1977e-05 | 3.104e-05 | 3.0144e-05 | 2.9287e-05 | 2.8466e-05 | 2.768e-05 | 2.6926e-05 | 2.6203e-05 | 2.5509e-05 | 2.4843e-05 | 2.4203e-05 | 2.3588e-05 | 2.2996e-05 | 2.2427e-05 | 2.1878e-05 | 2.1351e-05 | 2.0842e-05 | 2.0351e-05 | 1.9878e-05 | 1.9422e-05 | 1.8981e-05 | 1.8556e-05 | 1.8145e-05 | 1.7747e-05 | 1.7363e-05 | 1.6992e-05 | 1.6632e-05 | 1.6284e-05 | 1.5947e-05 | 0.031917
1900 | 4.1138 | 0.5003 | 0.14937 | 0.064135 | 0.033554 | 0.019877 | 0.012824 | 0.0088044 | 0.0063373 | 0.0047342 | 0.0036441 | 0.002875 | 0.0023153 | 0.0018975 | 0.0015786 | 0.0013306 | 0.0011343 | 0.00097677 | 0.00084866 | 0.00074327 | 0.00065566 | 0.00058214 | 0.00051992 | 0.00046684 | 0.00042125 | 0.00038183 | 0.00034754 | 0.00031755 | 0.00029118 | 0.00026788 | 0.00024721 | 0.00022879 | 0.00021231 | 0.00019752 | 0.00018419 | 0.00017214 | 0.00016122 | 0.00015129 | 0.00014223 | 0.00013396 | 0.00012638 | 0.00011941 | 0.000113 | 0.00010709 | 0.00010163 | 9.6572e-05 | 9.188e-05 | 8.752e-05 | 8.3461e-05 | 7.9677e-05 | 7.6144e-05 | 7.2841e-05 | 6.9747e-05 | 6.6847e-05 | 6.4123e-05 | 6.1563e-05 | 5.9153e-05 | 5.6883e-05 | 5.4741e-05 | 5.2718e-05 | 5.0806e-05 | 4.8996e-05 | 4.7282e-05 | 4.5657e-05 | 4.4115e-05 | 4.265e-05 | 4.1258e-05 | 3.9933e-05 | 3.8672e-05 | 3.747e-05 | 3.6324e-05 | 3.523e-05 | 3.4185e-05 | 3.3187e-05 | 3.2232e-05 | 3.1318e-05 | 3.0444e-05 | 2.9605e-05 | 2.8802e-05 | 2.8031e-05 | 2.7291e-05 | 2.6581e-05 | 2.5898e-05 | 2.5242e-05 | 2.4611e-05 | 2.4003e-05 | 2.3418e-05 | 2.2855e-05 | 2.2312e-05 | 2.1789e-05 | 2.1284e-05 | 2.0797e-05 | 2.0326e-05 | 1.9872e-05 | 1.9433e-05 | 1.9009e-05 | 1.8599e-05 | 1.8202e-05 | 1.7818e-05 | 1.7447e-05 | 1.7087e-05 | 0.033554
1850 | 4.3263 | 0.52603 | 0.1571 | 0.067485 | 0.035325 | 0.020938 | 0.013516 | 0.0092844 | 0.0066864 | 0.0049976 | 0.0038488 | 0.0030379 | 0.0024478 | 0.002007 | 0.0016704 | 0.0014085 | 0.0012012 | 0.0010348 | 0.00089946 | 0.00078805 | 0.00069541 | 0.00061765 | 0.00055182 | 0.00049565 | 0.00044739 | 0.00040565 | 0.00036933 | 0.00033756 | 0.00030961 | 0.00028492 | 0.000263 | 0.00024346 | 0.00022599 | 0.00021029 | 0.00019614 | 0.00018336 | 0.00017176 | 0.00016122 | 0.0001516 | 0.00014281 | 0.00013476 | 0.00012736 | 0.00012054 | 0.00011426 | 0.00010845 | 0.00010307 | 9.8081e-05 | 9.3443e-05 | 8.9124e-05 | 8.5098e-05 | 8.1337e-05 | 7.7821e-05 | 7.4527e-05 | 7.1438e-05 | 6.8538e-05 | 6.5811e-05 | 6.3244e-05 | 6.0825e-05 | 5.8542e-05 | 5.6386e-05 | 5.4348e-05 | 5.2419e-05 | 5.0591e-05 | 4.8859e-05 | 4.7214e-05 | 4.5652e-05 | 4.4166e-05 | 4.2753e-05 | 4.1407e-05 | 4.0124e-05 | 3.8901e-05 | 3.7733e-05 | 3.6618e-05 | 3.5552e-05 | 3.4533e-05 | 3.3557e-05 | 3.2623e-05 | 3.1728e-05 | 3.087e-05 | 3.0046e-05 | 2.9256e-05 | 2.8497e-05 | 2.7767e-05 | 2.7066e-05 | 2.6391e-05 | 2.5742e-05 | 2.5117e-05 | 2.4515e-05 | 2.3934e-05 | 2.3375e-05 | 2.2835e-05 | 2.2314e-05 | 2.1811e-05 | 2.1325e-05 | 2.0855e-05 | 2.0401e-05 | 1.9963e-05 | 1.9538e-05 | 1.9127e-05 | 1.873e-05 | 1.8344e-05 | 0.035325
1800 | 4.5564 | 0.55389 | 0.16547 | 0.071117 | 0.037247 | 0.02209 | 0.014268 | 0.0098064 | 0.0070663 | 0.0052844 | 0.0040718 | 0.0032156 | 0.0025922 | 0.0021264 | 0.0017706 | 0.0014937 | 0.0012744 | 0.0010983 | 0.00095501 | 0.00083705 | 0.00073893 | 0.00065654 | 0.00058676 | 0.00052722 | 0.00047604 | 0.00043176 | 0.00039323 | 0.0003595 | 0.00032984 | 0.00030362 | 0.00028034 | 0.00025958 | 0.00024101 | 0.00022432 | 0.00020929 | 0.00019569 | 0.00018336 | 0.00017214 | 0.00016191 | 0.00015255 | 0.00014398 | 0.0001361 | 0.00012884 | 0.00012215 | 0.00011596 | 0.00011023 | 0.00010491 | 9.9969e-05 | 9.5365e-05 | 9.1072e-05 | 8.7062e-05 | 8.3311e-05 | 7.9797e-05 | 7.6502e-05 | 7.3407e-05 | 7.0496e-05 | 6.7756e-05 | 6.5173e-05 | 6.2736e-05 | 6.0434e-05 | 5.8257e-05 | 5.6197e-05 | 5.4244e-05 | 5.2393e-05 | 5.0635e-05 | 4.8966e-05 | 4.7378e-05 | 4.5867e-05 | 4.4428e-05 | 4.3057e-05 | 4.1748e-05 | 4.05e-05 | 3.9307e-05 | 3.8167e-05 | 3.7076e-05 | 3.6032e-05 | 3.5032e-05 | 3.4074e-05 | 3.3156e-05 | 3.2274e-05 | 3.1428e-05 | 3.0615e-05 | 2.9834e-05 | 2.9083e-05 | 2.8361e-05 | 2.7665e-05 | 2.6996e-05 | 2.6351e-05 | 2.5729e-05 | 2.5129e-05 | 2.455e-05 | 2.3992e-05 | 2.3453e-05 | 2.2932e-05 | 2.2429e-05 | 2.1942e-05 | 2.1472e-05 | 2.1017e-05 | 2.0576e-05 | 2.015e-05 | 1.9737e-05 | 0.037247
1750 | 4.806 | 0.58413 | 0.17456 | 0.075064 | 0.039337 | 0.023344 | 0.015087 | 0.010375 | 0.0074806 | 0.0055974 | 0.0043154 | 0.0034097 | 0.0027501 | 0.002257 | 0.0018803 | 0.0015869 | 0.0013546 | 0.0011679 | 0.001016 | 0.00089082 | 0.00078669 | 0.00069924 | 0.00062515 | 0.00056191 | 0.00050753 | 0.00046048 | 0.00041952 | 0.00038366 | 0.0003521 | 0.0003242 | 0.00029943 | 0.00027734 | 0.00025756 | 0.00023979 | 0.00022377 | 0.00020929 | 0.00019614 | 0.00018419 | 0.00017328 | 0.0001633 | 0.00015415 | 0.00014575 | 0.00013801 | 0.00013087 | 0.00012426 | 0.00011814 | 0.00011246 | 0.00010718 | 0.00010226 | 9.7675e-05 | 9.339e-05 | 8.9381e-05 | 8.5625e-05 | 8.2102e-05 | 7.8792e-05 | 7.568e-05 | 7.2749e-05 | 6.9986e-05 | 6.7378e-05 | 6.4914e-05 | 6.2584e-05 | 6.0379e-05 | 5.8289e-05 | 5.6306e-05 | 5.4424e-05 | 5.2636e-05 | 5.0935e-05 | 4.9317e-05 | 4.7775e-05 | 4.6305e-05 | 4.4903e-05 | 4.3565e-05 | 4.2286e-05 | 4.1064e-05 | 3.9895e-05 | 3.8775e-05 | 3.7703e-05 | 3.6676e-05 | 3.569e-05 | 3.4745e-05 | 3.3837e-05 | 3.2965e-05 | 3.2127e-05 | 3.1321e-05 | 3.0545e-05 | 2.9799e-05 | 2.908e-05 | 2.8387e-05 | 2.772e-05 | 2.7076e-05 | 2.6454e-05 | 2.5855e-05 | 2.5276e-05 | 2.4716e-05 | 2.4176e-05 | 2.3653e-05 | 2.3147e-05 | 2.2658e-05 | 2.2185e-05 | 2.1727e-05 | 2.1283e-05 | 0.039337
1700 | 5.0776 | 0.61703 | 0.18446 | 0.079364 | 0.041616 | 0.024712 | 0.015981 | 0.010997 | 0.0079338 | 0.00594 | 0.0045821 | 0.0036225 | 0.0029232 | 0.0024004 | 0.0020007 | 0.0016894 | 0.0014427 | 0.0012444 | 0.001083 | 0.00094998 | 0.00083928 | 0.00074627 | 0.00066745 | 0.00060014 | 0.00054226 | 0.00049215 | 0.00044852 | 0.00041031 | 0.00037668 | 0.00034694 | 0.00032052 | 0.00029696 | 0.00027586 | 0.00025689 | 0.00023979 | 0.00022432 | 0.00021029 | 0.00019752 | 0.00018586 | 0.0001752 | 0.00016542 | 0.00015644 | 0.00014816 | 0.00014052 | 0.00013345 | 0.0001269 | 0.00012083 | 0.00011517 | 0.00010991 | 0.000105 | 0.00010041 | 9.6114e-05 | 9.209e-05 | 8.8314e-05 | 8.4768e-05 | 8.1431e-05 | 7.8289e-05 | 7.5327e-05 | 7.2531e-05 | 6.9888e-05 | 6.7389e-05 | 6.5023e-05 | 6.278e-05 | 6.0653e-05 | 5.8633e-05 | 5.6713e-05 | 5.4888e-05 | 5.315e-05 | 5.1494e-05 | 4.9916e-05 | 4.841e-05 | 4.6972e-05 | 4.5599e-05 | 4.4285e-05 | 4.3029e-05 | 4.1826e-05 | 4.0673e-05 | 3.9569e-05 | 3.8509e-05 | 3.7493e-05 | 3.6517e-05 | 3.5579e-05 | 3.4677e-05 | 3.381e-05 | 3.2976e-05 | 3.2173e-05 | 3.1399e-05 | 3.0654e-05 | 2.9935e-05 | 2.9242e-05 | 2.8574e-05 | 2.7928e-05 | 2.7305e-05 | 2.6702e-05 | 2.612e-05 | 2.5558e-05 | 2.5013e-05 | 2.4486e-05 | 2.3976e-05 | 2.3483e-05 | 2.3004e-05 | 0.041616
1650 | 5.3738 | 0.65291 | 0.19527 | 0.084061 | 0.044108 | 0.026209 | 0.01696 | 0.011679 | 0.008431 | 0.0063161 | 0.0048751 | 0.0038564 | 0.0031137 | 0.0025582 | 0.0021333 | 0.0018022 | 0.0015398 | 0.0013288 | 0.0011569 | 0.0010153 | 0.00089735 | 0.00079822 | 0.0007142 | 0.00064242 | 0.00058066 | 0.00052719 | 0.00048061 | 0.00043982 | 0.0004039 | 0.00037212 | 0.00034389 | 0.0003187 | 0.00029614 | 0.00027586 | 0.00025756 | 0.00024101 | 0.00022599 | 0.00021231 | 0.00019983 | 0.00018841 | 0.00017794 | 0.00016831 | 0.00015944 | 0.00015125 | 0.00014367 | 0.00013665 | 0.00013013 | 0.00012406 | 0.00011841 | 0.00011314 | 0.00010822 | 0.00010361 | 9.9284e-05 | 9.5229e-05 | 9.1419e-05 | 8.7835e-05 | 8.4459e-05 | 8.1275e-05 | 7.8269e-05 | 7.5429e-05 | 7.2742e-05 | 7.0197e-05 | 6.7785e-05 | 6.5497e-05 | 6.3324e-05 | 6.1258e-05 | 5.9293e-05 | 5.7423e-05 | 5.5641e-05 | 5.3942e-05 | 5.2321e-05 | 5.0772e-05 | 4.9293e-05 | 4.7878e-05 | 4.6525e-05 | 4.5229e-05 | 4.3987e-05 | 4.2797e-05 | 4.1655e-05 | 4.0559e-05 | 3.9507e-05 | 3.8496e-05 | 3.7524e-05 | 3.6589e-05 | 3.569e-05 | 3.4824e-05 | 3.3989e-05 | 3.3185e-05 | 3.241e-05 | 3.1662e-05 | 3.0941e-05 | 3.0244e-05 | 2.9571e-05 | 2.8921e-05 | 2.8293e-05 | 2.7685e-05 | 2.7098e-05 | 2.6529e-05 | 2.5978e-05 | 2.5445e-05 | 2.4929e-05 | 0.044108
1600 | 5.6978 | 0.69216 | 0.20709 | 0.089207 | 0.04684 | 0.027852 | 0.018036 | 0.012428 | 0.0089779 | 0.0067302 | 0.005198 | 0.0041143 | 0.0033239 | 0.0027324 | 0.0022798 | 0.001927 | 0.0016472 | 0.0014222 | 0.0012388 | 0.0010876 | 0.00096169 | 0.00085581 | 0.00076603 | 0.00068931 | 0.00062328 | 0.00056609 | 0.00051626 | 0.00047259 | 0.00043414 | 0.00040011 | 0.00036987 | 0.00034288 | 0.0003187 | 0.00029696 | 0.00027734 | 0.00025958 | 0.00024346 | 0.00022879 | 0.00021539 | 0.00020313 | 0.00019188 | 0.00018154 | 0.00017201 | 0.00016321 | 0.00015507 | 0.00014752 | 0.00014051 | 0.00013398 | 0.00012791 | 0.00012223 | 0.00011693 | 0.00011197 | 0.00010732 | 0.00010295 | 9.885e-05 | 9.4989e-05 | 9.1352e-05 | 8.7922e-05 | 8.4683e-05 | 8.1622e-05 | 7.8725e-05 | 7.5982e-05 | 7.3381e-05 | 7.0914e-05 | 6.857e-05 | 6.6342e-05 | 6.4222e-05 | 6.2204e-05 | 6.0281e-05 | 5.8447e-05 | 5.6697e-05 | 5.5025e-05 | 5.3428e-05 | 5.1901e-05 | 5.0439e-05 | 4.9039e-05 | 4.7698e-05 | 4.6412e-05 | 4.5178e-05 | 4.3994e-05 | 4.2857e-05 | 4.1764e-05 | 4.0713e-05 | 3.9703e-05 | 3.873e-05 | 3.7793e-05 | 3.6891e-05 | 3.6022e-05 | 3.5183e-05 | 3.4374e-05 | 3.3594e-05 | 3.284e-05 | 3.2112e-05 | 3.1409e-05 | 3.0728e-05 | 3.0071e-05 | 2.9435e-05 | 2.8819e-05 | 2.8223e-05 | 2.7646e-05 | 2.7086e-05 | 0.04684
1550 | 6.0531 | 0.73521 | 0.22008 | 0.094861 | 0.049845 | 0.02966 | 0.019222 | 0.013255 | 0.0095817 | 0.0071877 | 0.005555 | 0.0043996 | 0.0035565 | 0.0029253 | 0.0024422 | 0.0020653 | 0.0017664 | 0.0015259 | 0.0013297 | 0.001168 | 0.0010332 | 0.00091988 | 0.00082371 | 0.00074151 | 0.00067075 | 0.00060943 | 0.00055598 | 0.00050914 | 0.00046787 | 0.00043134 | 0.00039886 | 0.00036987 | 0.00034389 | 0.00032052 | 0.00029943 | 0.00028034 | 0.000263 | 0.00024721 | 0.00023279 | 0.0002196 | 0.00020749 | 0.00019635 | 0.00018608 | 0.0001766 | 0.00016782 | 0.00015968 | 0.00015213 | 0.00014509 | 0.00013854 | 0.00013242 | 0.0001267 | 0.00012135 | 0.00011632 | 0.00011161 | 0.00010718 | 0.00010301 | 9.9084e-05 | 9.5378e-05 | 9.1879e-05 | 8.857e-05 | 8.544e-05 | 8.2474e-05 | 7.9662e-05 | 7.6994e-05 | 7.4459e-05 | 7.2049e-05 | 6.9756e-05 | 6.7573e-05 | 6.5492e-05 | 6.3507e-05 | 6.1613e-05 | 5.9803e-05 | 5.8074e-05 | 5.642e-05 | 5.4837e-05 | 5.3321e-05 | 5.1868e-05 | 5.0475e-05 | 4.9138e-05 | 4.7855e-05 | 4.6622e-05 | 4.5438e-05 | 4.4299e-05 | 4.3204e-05 | 4.2149e-05 | 4.1134e-05 | 4.0155e-05 | 3.9212e-05 | 3.8303e-05 | 3.7425e-05 | 3.6578e-05 | 3.5761e-05 | 3.4971e-05 | 3.4207e-05 | 3.3469e-05 | 3.2755e-05 | 3.2065e-05 | 3.1397e-05 | 3.0749e-05 | 3.0123e-05 | 2.9515e-05 | 0.049845
1500 | 6.444 | 0.7826 | 0.23438 | 0.1011 | 0.053161 | 0.031659 | 0.020532 | 0.014169 | 0.01025 | 0.0076949 | 0.0059511 | 0.0047164 | 0.003815 | 0.0031399 | 0.0026229 | 0.0022193 | 0.0018992 | 0.0016414 | 0.0014312 | 0.0012577 | 0.0011131 | 0.0009914 | 0.00088815 | 0.00079985 | 0.00072381 | 0.00065789 | 0.00060042 | 0.00055003 | 0.00050562 | 0.0004663 | 0.00043134 | 0.00040011 | 0.00037212 | 0.00034694 | 0.0003242 | 0.00030362 | 0.00028492 | 0.00026788 | 0.00025233 | 0.00023808 | 0.00022501 | 0.00021298 | 0.00020189 | 0.00019164 | 0.00018216 | 0.00017336 | 0.00016519 | 0.00015759 | 0.0001505 | 0.00014388 | 0.00013769 | 0.00013189 | 0.00012646 | 0.00012136 | 0.00011656 | 0.00011204 | 0.00010779 | 0.00010377 | 9.9983e-05 | 9.6397e-05 | 9.3004e-05 | 8.9789e-05 | 8.674e-05 | 8.3846e-05 | 8.1097e-05 | 7.8483e-05 | 7.5995e-05 | 7.3625e-05 | 7.1367e-05 | 6.9213e-05 | 6.7156e-05 | 6.5192e-05 | 6.3314e-05 | 6.1518e-05 | 5.9798e-05 | 5.8151e-05 | 5.6573e-05 | 5.5059e-05 | 5.3607e-05 | 5.2213e-05 | 5.0873e-05 | 4.9586e-05 | 4.8347e-05 | 4.7156e-05 | 4.6009e-05 | 4.4905e-05 | 4.3841e-05 | 4.2815e-05 | 4.1826e-05 | 4.0871e-05 | 3.995e-05 | 3.906e-05 | 3.82e-05 | 3.7369e-05 | 3.6566e-05 | 3.5789e-05 | 3.5037e-05 | 3.4309e-05 | 3.3605e-05 | 3.2922e-05 | 3.2261e-05 | 0.053161
1450 | 6.8755 | 0.83493 | 0.25018 | 0.10799 | 0.056834 | 0.033874 | 0.021987 | 0.015186 | 0.010994 | 0.0082593 | 0.0063922 | 0.0050695 | 0.0041034 | 0.0033793 | 0.0028246 | 0.0023915 | 0.0020476 | 0.0017707 | 0.0015447 | 0.0013581 | 0.0012026 | 0.0010716 | 0.00096042 | 0.00086531 | 0.00078337 | 0.00071232 | 0.00065034 | 0.00059598 | 0.00054806 | 0.00050562 | 0.00046787 | 0.00043414 | 0.0004039 | 0.00037668 | 0.0003521 | 0.00032984 | 0.00030961 | 0.00029118 | 0.00027434 | 0.00025892 | 0.00024476 | 0.00023173 | 0.00021972 | 0.00020862 | 0.00019834 | 0.0001888 | 0.00017994 | 0.00017169 | 0.000164 | 0.00015682 | 0.0001501 | 0.00014381 | 0.00013791 | 0.00013237 | 0.00012716 | 0.00012226 | 0.00011763 | 0.00011327 | 0.00010915 | 0.00010525 | 0.00010156 | 9.8065e-05 | 9.4749e-05 | 9.1601e-05 | 8.861e-05 | 8.5765e-05 | 8.3057e-05 | 8.0478e-05 | 7.802e-05 | 7.5674e-05 | 7.3435e-05 | 7.1296e-05 | 6.925e-05 | 6.7293e-05 | 6.542e-05 | 6.3625e-05 | 6.1905e-05 | 6.0255e-05 | 5.8672e-05 | 5.7152e-05 | 5.5691e-05 | 5.4287e-05 | 5.2937e-05 | 5.1638e-05 | 5.0387e-05 | 4.9182e-05 | 4.8021e-05 | 4.6901e-05 | 4.5822e-05 | 4.478e-05 | 4.3774e-05 | 4.2802e-05 | 4.1864e-05 | 4.0957e-05 | 4.0079e-05 | 3.9231e-05 | 3.841e-05 | 3.7615e-05 | 3.6845e-05 | 3.6099e-05 | 3.5377e-05 | 0.056834
1400 | 7.3535 | 0.89292 | 0.26771 | 0.11565 | 0.060918 | 0.03634 | 0.023608 | 0.016319 | 0.011824 | 0.00889 | 0.0068855 | 0.0054647 | 0.0044263 | 0.0036477 | 0.0030509 | 0.0025847 | 0.0022144 | 0.0019159 | 0.0016723 | 0.0014711 | 0.0013032 | 0.0011619 | 0.0010418 | 0.00093907 | 0.00085051 | 0.00077369 | 0.00070666 | 0.00064785 | 0.00059598 | 0.00055003 | 0.00050914 | 0.00047259 | 0.00043982 | 0.00041031 | 0.00038366 | 0.0003595 | 0.00033756 | 0.00031755 | 0.00029927 | 0.00028252 | 0.00026714 | 0.00025299 | 0.00023993 | 0.00022786 | 0.00021668 | 0.00020631 | 0.00019667 | 0.0001877 | 0.00017933 | 0.00017151 | 0.00016419 | 0.00015734 | 0.00015092 | 0.00014488 | 0.0001392 | 0.00013385 | 0.00012881 | 0.00012406 | 0.00011956 | 0.00011531 | 0.00011129 | 0.00010747 | 0.00010385 | 0.00010042 | 9.7152e-05 | 9.4046e-05 | 9.109e-05 | 8.8273e-05 | 8.5587e-05 | 8.3025e-05 | 8.0578e-05 | 7.824e-05 | 7.6005e-05 | 7.3866e-05 | 7.1818e-05 | 6.9856e-05 | 6.7975e-05 | 6.617e-05 | 6.4439e-05 | 6.2776e-05 | 6.1178e-05 | 5.9642e-05 | 5.8164e-05 | 5.6742e-05 | 5.5373e-05 | 5.4054e-05 | 5.2782e-05 | 5.1557e-05 | 5.0374e-05 | 4.9233e-05 | 4.8132e-05 | 4.7068e-05 | 4.6039e-05 | 4.5045e-05 | 4.4084e-05 | 4.3154e-05 | 4.2254e-05 | 4.1383e-05 | 4.0539e-05 | 3.9722e-05 | 3.893e-05 | 0.060918
1350 | 7.8851 | 0.95744 | 0.28724 | 0.12419 | 0.065476 | 0.039095 | 0.025422 | 0.017588 | 0.012755 | 0.0095977 | 0.0074395 | 0.0059089 | 0.0047897 | 0.0039499 | 0.0033059 | 0.0028025 | 0.0024024 | 0.0020799 | 0.0018164 | 0.0015988 | 0.0014171 | 0.001264 | 0.0011339 | 0.0010226 | 0.00092656 | 0.00084324 | 0.0007705 | 0.00070666 | 0.00065034 | 0.00060042 | 0.00055598 | 0.00051626 | 0.00048061 | 0.00044852 | 0.00041952 | 0.00039323 | 0.00036933 | 0.00034754 | 0.00032763 | 0.00030938 | 0.00029261 | 0.00027718 | 0.00026294 | 0.00024977 | 0.00023758 | 0.00022626 | 0.00021573 | 0.00020593 | 0.00019679 | 0.00018825 | 0.00018026 | 0.00017277 | 0.00016575 | 0.00015915 | 0.00015294 | 0.00014709 | 0.00014158 | 0.00013637 | 0.00013145 | 0.0001268 | 0.00012239 | 0.00011822 | 0.00011425 | 0.00011049 | 0.00010691 | 0.00010351 | 0.00010027 | 9.7181e-05 | 9.4238e-05 | 9.1428e-05 | 8.8745e-05 | 8.6181e-05 | 8.3729e-05 | 8.1383e-05 | 7.9136e-05 | 7.6982e-05 | 7.4918e-05 | 7.2938e-05 | 7.1037e-05 | 6.9211e-05 | 6.7456e-05 | 6.5769e-05 | 6.4146e-05 | 6.2584e-05 | 6.108e-05 | 5.9631e-05 | 5.8234e-05 | 5.6887e-05 | 5.5588e-05 | 5.4333e-05 | 5.3122e-05 | 5.1952e-05 | 5.0822e-05 | 4.9729e-05 | 4.8672e-05 | 4.7649e-05 | 4.6659e-05 | 4.57e-05 | 4.4772e-05 | 4.3873e-05 | 4.3001e-05 | 0.065476
1300 | 8.4787 | 1.0295 | 0.30908 | 0.13376 | 0.070587 | 0.042189 | 0.02746 | 0.019016 | 0.013803 | 0.010396 | 0.0080648 | 0.0064107 | 0.0052004 | 0.0042918 | 0.0035945 | 0.0030492 | 0.0026156 | 0.0022659 | 0.00198 | 0.0017437 | 0.0015464 | 0.0013801 | 0.0012387 | 0.0011176 | 0.0010131 | 0.00092244 | 0.00084324 | 0.00077369 | 0.00071232 | 0.00065789 | 0.00060943 | 0.00056609 | 0.00052719 | 0.00049215 | 0.00046048 | 0.00043176 | 0.00040565 | 0.00038183 | 0.00036006 | 0.0003401 | 0.00032176 | 0.00030486 | 0.00028928 | 0.00027486 | 0.0002615 | 0.0002491 | 0.00023757 | 0.00022683 | 0.00021681 | 0.00020744 | 0.00019868 | 0.00019046 | 0.00018275 | 0.00017551 | 0.00016869 | 0.00016227 | 0.00015622 | 0.0001505 | 0.0001451 | 0.00013998 | 0.00013514 | 0.00013055 | 0.00012619 | 0.00012206 | 0.00011812 | 0.00011438 | 0.00011081 | 0.00010742 | 0.00010418 | 0.00010108 | 9.8131e-05 | 9.5308e-05 | 9.2608e-05 | 9.0024e-05 | 8.7549e-05 | 8.5177e-05 | 8.2902e-05 | 8.072e-05 | 7.8625e-05 | 7.6613e-05 | 7.4678e-05 | 7.2818e-05 | 7.1029e-05 | 6.9306e-05 | 6.7647e-05 | 6.6049e-05 | 6.4508e-05 | 6.3022e-05 | 6.1588e-05 | 6.0204e-05 | 5.8867e-05 | 5.7576e-05 | 5.6328e-05 | 5.5121e-05 | 5.3954e-05 | 5.2825e-05 | 5.1731e-05 | 5.0673e-05 | 4.9647e-05 | 4.8654e-05 | 4.769e-05 | 0.070587
1250 | 9.1444 | 1.1104 | 0.33362 | 0.14452 | 0.076345 | 0.045679 | 0.029762 | 0.020631 | 0.01499 | 0.0113 | 0.0087741 | 0.0069804 | 0.0056671 | 0.0046806 | 0.0039231 | 0.0033303 | 0.0028586 | 0.002478 | 0.0021667 | 0.0019093 | 0.0016942 | 0.0015128 | 0.0013585 | 0.0012263 | 0.0011122 | 0.0010131 | 0.00092656 | 0.00085051 | 0.00078337 | 0.00072381 | 0.00067075 | 0.00062328 | 0.00058066 | 0.00054226 | 0.00050753 | 0.00047604 | 0.00044739 | 0.00042125 | 0.00039735 | 0.00037543 | 0.00035528 | 0.00033672 | 0.00031959 | 0.00030374 | 0.00028905 | 0.00027541 | 0.00026272 | 0.0002509 | 0.00023987 | 0.00022956 | 0.00021991 | 0.00021086 | 0.00020237 | 0.00019438 | 0.00018687 | 0.00017979 | 0.00017311 | 0.00016681 | 0.00016085 | 0.00015521 | 0.00014986 | 0.00014479 | 0.00013998 | 0.00013541 | 0.00013107 | 0.00012693 | 0.000123 | 0.00011924 | 0.00011566 | 0.00011224 | 0.00010898 | 0.00010586 | 0.00010287 | 0.00010001 | 9.7277e-05 | 9.4653e-05 | 9.2136e-05 | 8.9721e-05 | 8.7402e-05 | 8.5175e-05 | 8.3034e-05 | 8.0974e-05 | 7.8993e-05 | 7.7085e-05 | 7.5247e-05 | 7.3477e-05 | 7.177e-05 | 7.0123e-05 | 6.8534e-05 | 6.7e-05 | 6.5518e-05 | 6.4087e-05 | 6.2703e-05 | 6.1365e-05 | 6.0071e-05 | 5.8819e-05 | 5.7606e-05 | 5.6432e-05 | 5.5294e-05 | 5.4192e-05 | 5.3123e-05 | 0.076345
1200 | 9.8946 | 1.2017 | 0.36133 | 0.15668 | 0.082867 | 0.049636 | 0.032377 | 0.022468 | 0.016341 | 0.01233 | 0.0095831 | 0.0076309 | 0.0062005 | 0.0051253 | 0.0042991 | 0.0036522 | 0.0031372 | 0.0027212 | 0.002381 | 0.0020994 | 0.001864 | 0.0016654 | 0.0014964 | 0.0013514 | 0.0012263 | 0.0011176 | 0.0010226 | 0.00093907 | 0.00086531 | 0.00079985 | 0.00074151 | 0.00068931 | 0.00064242 | 0.00060014 | 0.00056191 | 0.00052722 | 0.00049565 | 0.00046684 | 0.00044049 | 0.00041631 | 0.00039408 | 0.0003736 | 0.00035469 | 0.00033719 | 0.00032097 | 0.0003059 | 0.00029188 | 0.00027881 | 0.00026661 | 0.00025521 | 0.00024453 | 0.00023452 | 0.00022512 | 0.00021628 | 0.00020796 | 0.00020012 | 0.00019273 | 0.00018574 | 0.00017914 | 0.00017288 | 0.00016696 | 0.00016134 | 0.000156 | 0.00015094 | 0.00014612 | 0.00014153 | 0.00013716 | 0.00013299 | 0.00012902 | 0.00012522 | 0.0001216 | 0.00011813 | 0.00011481 | 0.00011164 | 0.00010859 | 0.00010568 | 0.00010288 | 0.0001002 | 9.7617e-05 | 9.514e-05 | 9.2759e-05 | 9.0468e-05 | 8.8264e-05 | 8.6141e-05 | 8.4097e-05 | 8.2126e-05 | 8.0226e-05 | 7.8393e-05 | 7.6624e-05 | 7.4916e-05 | 7.3266e-05 | 7.1672e-05 | 7.0131e-05 | 6.8641e-05 | 6.7199e-05 | 6.5803e-05 | 6.4452e-05 | 6.3144e-05 | 6.1876e-05 | 6.0647e-05 | 5.9456e-05 | 0.082867
1150 | 10.7445 | 1.3051 | 0.39279 | 0.17052 | 0.090294 | 0.054151 | 0.035363 | 0.024568 | 0.017888 | 0.013511 | 0.010512 | 0.0083781 | 0.0068138 | 0.005637 | 0.0047322 | 0.0040232 | 0.0034585 | 0.0030021 | 0.0026284 | 0.0023191 | 0.0020603 | 0.0018419 | 0.0016559 | 0.0014964 | 0.0013585 | 0.0012387 | 0.0011339 | 0.0010418 | 0.00096042 | 0.00088815 | 0.00082371 | 0.00076603 | 0.0007142 | 0.00066745 | 0.00062515 | 0.00058676 | 0.00055182 | 0.00051992 | 0.00049072 | 0.00046393 | 0.00043929 | 0.00041658 | 0.0003956 | 0.00037619 | 0.00035818 | 0.00034145 | 0.00032588 | 0.00031137 | 0.00029782 | 0.00028514 | 0.00027327 | 0.00026214 | 0.00025169 | 0.00024186 | 0.0002326 | 0.00022388 | 0.00021565 | 0.00020787 | 0.00020051 | 0.00019355 | 0.00018695 | 0.00018069 | 0.00017474 | 0.00016909 | 0.00016372 | 0.0001586 | 0.00015373 | 0.00014908 | 0.00014464 | 0.00014041 | 0.00013636 | 0.00013249 | 0.00012879 | 0.00012524 | 0.00012185 | 0.00011859 | 0.00011546 | 0.00011247 | 0.00010958 | 0.00010682 | 0.00010415 | 0.00010159 | 9.9129e-05 | 9.6755e-05 | 9.4469e-05 | 9.2265e-05 | 9.0139e-05 | 8.8089e-05 | 8.6109e-05 | 8.4198e-05 | 8.2352e-05 | 8.0567e-05 | 7.8842e-05 | 7.7174e-05 | 7.5559e-05 | 7.3997e-05 | 7.2483e-05 | 7.1018e-05 | 6.9598e-05 | 6.8221e-05 | 6.6886e-05 | 0.090294
1100 | 11.7127 | 1.4231 | 0.42874 | 0.18636 | 0.098806 | 0.059332 | 0.038795 | 0.026985 | 0.019671 | 0.014874 | 0.011584 | 0.0092421 | 0.0075236 | 0.0062299 | 0.0052344 | 0.0044538 | 0.0038316 | 0.0033284 | 0.0029163 | 0.0025748 | 0.002289 | 0.0020475 | 0.0018419 | 0.0016654 | 0.0015128 | 0.0013801 | 0.001264 | 0.0011619 | 0.0010716 | 0.0009914 | 0.00091988 | 0.00085581 | 0.00079822 | 0.00074627 | 0.00069924 | 0.00065654 | 0.00061765 | 0.00058214 | 0.00054963 | 0.00051978 | 0.00049233 | 0.00046702 | 0.00044363 | 0.00042197 | 0.00040188 | 0.00038322 | 0.00036584 | 0.00034963 | 0.00033449 | 0.00032034 | 0.00030707 | 0.00029463 | 0.00028294 | 0.00027195 | 0.0002616 | 0.00025184 | 0.00024262 | 0.00023392 | 0.00022568 | 0.00021788 | 0.00021049 | 0.00020347 | 0.00019681 | 0.00019048 | 0.00018446 | 0.00017872 | 0.00017326 | 0.00016804 | 0.00016307 | 0.00015832 | 0.00015378 | 0.00014943 | 0.00014528 | 0.0001413 | 0.00013748 | 0.00013382 | 0.00013031 | 0.00012694 | 0.00012371 | 0.00012059 | 0.0001176 | 0.00011472 | 0.00011195 | 0.00010929 | 0.00010671 | 0.00010424 | 0.00010184 | 9.9538e-05 | 9.7311e-05 | 9.516e-05 | 9.3083e-05 | 9.1074e-05 | 8.9133e-05 | 8.7254e-05 | 8.5437e-05 | 8.3677e-05 | 8.1973e-05 | 8.0323e-05 | 7.8723e-05 | 7.7172e-05 | 7.5669e-05 | 0.098806
1050 | 12.8226 | 1.5586 | 0.47006 | 0.20459 | 0.10863 | 0.06532 | 0.042768 | 0.029787 | 0.02174 | 0.016459 | 0.012832 | 0.010249 | 0.0083513 | 0.0069218 | 0.0058211 | 0.0049572 | 0.0042682 | 0.0037106 | 0.0032535 | 0.0028746 | 0.0025572 | 0.002289 | 0.0020603 | 0.001864 | 0.0016942 | 0.0015464 | 0.0014171 | 0.0013032 | 0.0012026 | 0.0011131 | 0.0010332 | 0.00096169 | 0.00089735 | 0.00083928 | 0.00078669 | 0.00073893 | 0.00069541 | 0.00065566 | 0.00061925 | 0.00058582 | 0.00055505 | 0.00052668 | 0.00050045 | 0.00047616 | 0.00045362 | 0.00043266 | 0.00041315 | 0.00039495 | 0.00037794 | 0.00036203 | 0.00034713 | 0.00033314 | 0.00031999 | 0.00030763 | 0.00029598 | 0.000285 | 0.00027462 | 0.00026482 | 0.00025555 | 0.00024676 | 0.00023843 | 0.00023053 | 0.00022302 | 0.00021588 | 0.00020909 | 0.00020262 | 0.00019645 | 0.00019057 | 0.00018496 | 0.0001796 | 0.00017447 | 0.00016957 | 0.00016487 | 0.00016038 | 0.00015607 | 0.00015193 | 0.00014797 | 0.00014416 | 0.0001405 | 0.00013698 | 0.0001336 | 0.00013035 | 0.00012721 | 0.00012419 | 0.00012129 | 0.00011848 | 0.00011578 | 0.00011317 | 0.00011064 | 0.00010821 | 0.00010586 | 0.00010358 | 0.00010139 | 9.9258e-05 | 9.7199e-05 | 9.5206e-05 | 9.3275e-05 | 9.1405e-05 | 8.9592e-05 | 8.7835e-05 | 8.6131e-05 | 0.10863
1000 | 14.1037 | 1.7151 | 0.51792 | 0.22575 | 0.12004 | 0.072294 | 0.047403 | 0.033061 | 0.024161 | 0.018314 | 0.014296 | 0.01143 | 0.0093243 | 0.007736 | 0.006512 | 0.0055507 | 0.0047833 | 0.0041618 | 0.003652 | 0.003229 | 0.0028746 | 0.0025748 | 0.0023191 | 0.0020994 | 0.0019093 | 0.0017437 | 0.0015988 | 0.0014711 | 0.0013581 | 0.0012577 | 0.001168 | 0.0010876 | 0.0010153 | 0.00094998 | 0.00089082 | 0.00083705 | 0.00078805 | 0.00074327 | 0.00070224 | 0.00066456 | 0.00062986 | 0.00059785 | 0.00056825 | 0.00054083 | 0.00051537 | 0.0004917 | 0.00046966 | 0.00044908 | 0.00042986 | 0.00041187 | 0.000395 | 0.00037917 | 0.0003643 | 0.0003503 | 0.00033711 | 0.00032466 | 0.00031291 | 0.0003018 | 0.00029129 | 0.00028133 | 0.00027188 | 0.00026292 | 0.0002544 | 0.0002463 | 0.00023859 | 0.00023125 | 0.00022425 | 0.00021757 | 0.00021119 | 0.0002051 | 0.00019928 | 0.0001937 | 0.00018837 | 0.00018326 | 0.00017836 | 0.00017366 | 0.00016914 | 0.00016481 | 0.00016065 | 0.00015665 | 0.0001528 | 0.00014909 | 0.00014553 | 0.00014209 | 0.00013878 | 0.00013558 | 0.0001325 | 0.00012953 | 0.00012665 | 0.00012388 | 0.0001212 | 0.00011861 | 0.0001161 | 0.00011368 | 0.00011133 | 0.00010905 | 0.00010685 | 0.00010472 | 0.00010265 | 0.00010065 | 9.8702e-05 | 0.12004
950 | 15.5934 | 1.8975 | 0.57378 | 0.25051 | 0.13343 | 0.080483 | 0.052855 | 0.036918 | 0.027018 | 0.020507 | 0.016028 | 0.01283 | 0.010478 | 0.0087027 | 0.0073331 | 0.0062566 | 0.0053965 | 0.0046993 | 0.0041271 | 0.003652 | 0.0032535 | 0.0029163 | 0.0026284 | 0.002381 | 0.0021667 | 0.00198 | 0.0018164 | 0.0016723 | 0.0015447 | 0.0014312 | 0.0013297 | 0.0012388 | 0.0011569 | 0.001083 | 0.001016 | 0.00095501 | 0.00089946 | 0.00084866 | 0.0008021 | 0.00075932 | 0.00071992 | 0.00068356 | 0.00064992 | 0.00061875 | 0.0005898 | 0.00056287 | 0.00053779 | 0.00051437 | 0.00049248 | 0.00047199 | 0.00045277 | 0.00043473 | 0.00041777 | 0.00040181 | 0.00038677 | 0.00037257 | 0.00035916 | 0.00034648 | 0.00033448 | 0.00032311 | 0.00031232 | 0.00030207 | 0.00029234 | 0.00028308 | 0.00027427 | 0.00026587 | 0.00025787 | 0.00025023 | 0.00024293 | 0.00023596 | 0.00022929 | 0.00022292 | 0.00021681 | 0.00021095 | 0.00020534 | 0.00019996 | 0.00019479 | 0.00018982 | 0.00018505 | 0.00018047 | 0.00017605 | 0.0001718 | 0.00016771 | 0.00016377 | 0.00015997 | 0.00015631 | 0.00015277 | 0.00014936 | 0.00014606 | 0.00014288 | 0.0001398 | 0.00013682 | 0.00013394 | 0.00013116 | 0.00012846 | 0.00012585 | 0.00012332 | 0.00012087 | 0.00011849 | 0.00011619 | 0.00011395 | 0.13343
900 | 17.3403 | 2.1118 | 0.63957 | 0.27972 | 0.14926 | 0.090189 | 0.059329 | 0.041506 | 0.030422 | 0.023124 | 0.018097 | 0.014506 | 0.01186 | 0.0098618 | 0.0083187 | 0.0071047 | 0.0061338 | 0.0053463 | 0.0046993 | 0.0041618 | 0.0037106 | 0.0033284 | 0.0030021 | 0.0027212 | 0.002478 | 0.0022659 | 0.0020799 | 0.0019159 | 0.0017707 | 0.0016414 | 0.0015259 | 0.0014222 | 0.0013288 | 0.0012444 | 0.0011679 | 0.0010983 | 0.0010348 | 0.00097677 | 0.00092353 | 0.00087458 | 0.00082949 | 0.00078786 | 0.00074933 | 0.00071361 | 0.00068044 | 0.00064957 | 0.00062079 | 0.00059393 | 0.0005688 | 0.00054528 | 0.00052321 | 0.00050249 | 0.00048301 | 0.00046466 | 0.00044736 | 0.00043104 | 0.00041562 | 0.00040103 | 0.00038722 | 0.00037412 | 0.0003617 | 0.00034991 | 0.00033869 | 0.00032803 | 0.00031787 | 0.00030819 | 0.00029896 | 0.00029015 | 0.00028174 | 0.0002737 | 0.00026601 | 0.00025864 | 0.00025159 | 0.00024484 | 0.00023836 | 0.00023214 | 0.00022617 | 0.00022043 | 0.00021492 | 0.00020962 | 0.00020452 | 0.00019961 | 0.00019488 | 0.00019032 | 0.00018593 | 0.00018169 | 0.0001776 | 0.00017365 | 0.00016983 | 0.00016615 | 0.00016259 | 0.00015914 | 0.00015581 | 0.00015258 | 0.00014946 | 0.00014644 | 0.00014351 | 0.00014067 | 0.00013791 | 0.00013524 | 0.00013265 | 0.14926
850 | 19.4078 | 2.366 | 0.71782 | 0.31456 | 0.16817 | 0.10182 | 0.0671 | 0.047024 | 0.034522 | 0.026281 | 0.020597 | 0.016532 | 0.013534 | 0.011267 | 0.0095151 | 0.0081352 | 0.0070306 | 0.0061338 | 0.0053965 | 0.0047833 | 0.0042682 | 0.0038316 | 0.0034585 | 0.0031372 | 0.0028586 | 0.0026156 | 0.0024024 | 0.0022144 | 0.0020476 | 0.0018992 | 0.0017664 | 0.0016472 | 0.0015398 | 0.0014427 | 0.0013546 | 0.0012744 | 0.0012012 | 0.0011343 | 0.0010729 | 0.0010164 | 0.00096435 | 0.00091626 | 0.00087175 | 0.00083046 | 0.00079211 | 0.0007564 | 0.0007231 | 0.00069201 | 0.00066292 | 0.00063567 | 0.00061011 | 0.0005861 | 0.00056351 | 0.00054224 | 0.00052218 | 0.00050324 | 0.00048534 | 0.00046841 | 0.00045237 | 0.00043716 | 0.00042273 | 0.00040902 | 0.00039599 | 0.00038359 | 0.00037178 | 0.00036053 | 0.00034979 | 0.00033954 | 0.00032975 | 0.00032039 | 0.00031143 | 0.00030286 | 0.00029465 | 0.00028678 | 0.00027923 | 0.00027198 | 0.00026502 | 0.00025834 | 0.00025191 | 0.00024573 | 0.00023978 | 0.00023405 | 0.00022853 | 0.00022321 | 0.00021809 | 0.00021314 | 0.00020836 | 0.00020375 | 0.0001993 | 0.000195 | 0.00019083 | 0.00018681 | 0.00018292 | 0.00017915 | 0.0001755 | 0.00017196 | 0.00016854 | 0.00016522 | 0.000162 | 0.00015888 | 0.00015585 | 0.16817
800 | 21.8804 | 2.6709 | 0.81192 | 0.35657 | 0.19105 | 0.11591 | 0.076538 | 0.053738 | 0.039521 | 0.030136 | 0.023655 | 0.019014 | 0.015587 | 0.012993 | 0.010986 | 0.0094031 | 0.0081352 | 0.0071047 | 0.0062566 | 0.0055507 | 0.0049572 | 0.0044538 | 0.0040232 | 0.0036522 | 0.0033303 | 0.0030492 | 0.0028025 | 0.0025847 | 0.0023915 | 0.0022193 | 0.0020653 | 0.001927 | 0.0018022 | 0.0016894 | 0.0015869 | 0.0014937 | 0.0014085 | 0.0013306 | 0.001259 | 0.0011932 | 0.0011325 | 0.0010764 | 0.0010245 | 0.00097628 | 0.00093149 | 0.00088978 | 0.00085087 | 0.00081452 | 0.00078051 | 0.00074864 | 0.00071873 | 0.00069062 | 0.00066417 | 0.00063926 | 0.00061575 | 0.00059356 | 0.00057258 | 0.00055272 | 0.00053391 | 0.00051607 | 0.00049914 | 0.00048305 | 0.00046775 | 0.00045319 | 0.00043932 | 0.00042609 | 0.00041348 | 0.00040143 | 0.00038992 | 0.00037891 | 0.00036838 | 0.0003583 | 0.00034864 | 0.00033937 | 0.00033049 | 0.00032196 | 0.00031377 | 0.00030589 | 0.00029832 | 0.00029104 | 0.00028403 | 0.00027728 | 0.00027078 | 0.00026451 | 0.00025846 | 0.00025263 | 0.00024699 | 0.00024156 | 0.0002363 | 0.00023122 | 0.00022631 | 0.00022156 | 0.00021697 | 0.00021252 | 0.00020821 | 0.00020404 | 0.00019999 | 0.00019607 | 0.00019227 | 0.00018858 | 0.000185 | 0.19105
750 | 24.8725 | 3.041 | 0.92653 | 0.40789 | 0.21907 | 0.13321 | 0.088156 | 0.062022 | 0.045699 | 0.034909 | 0.027447 | 0.022096 | 0.018141 | 0.015142 | 0.012819 | 0.010986 | 0.0095151 | 0.0083187 | 0.0073331 | 0.006512 | 0.0058211 | 0.0052344 | 0.0047322 | 0.0042991 | 0.0039231 | 0.0035945 | 0.0033059 | 0.0030509 | 0.0028246 | 0.0026229 | 0.0024422 | 0.0022798 | 0.0021333 | 0.0020007 | 0.0018803 | 0.0017706 | 0.0016704 | 0.0015786 | 0.0014944 | 0.0014168 | 0.0013453 | 0.0012791 | 0.0012178 | 0.0011609 | 0.001108 | 0.0010588 | 0.0010128 | 0.00096982 | 0.0009296 | 0.00089189 | 0.00085649 | 0.00082322 | 0.0007919 | 0.00076238 | 0.00073454 | 0.00070823 | 0.00068335 | 0.0006598 | 0.00063749 | 0.00061632 | 0.00059622 | 0.00057712 | 0.00055896 | 0.00054166 | 0.00052518 | 0.00050947 | 0.00049447 | 0.00048015 | 0.00046646 | 0.00045337 | 0.00044084 | 0.00042884 | 0.00041734 | 0.00040632 | 0.00039574 | 0.00038558 | 0.00037582 | 0.00036644 | 0.00035742 | 0.00034874 | 0.00034039 | 0.00033234 | 0.00032459 | 0.00031711 | 0.0003099 | 0.00030294 | 0.00029622 | 0.00028973 | 0.00028346 | 0.0002774 | 0.00027154 | 0.00026587 | 0.00026038 | 0.00025507 | 0.00024992 | 0.00024494 | 0.0002401 | 0.00023542 | 0.00023088 | 0.00022647 | 0.00022219 | 0.21907
700 | 28.5422 | 3.4966 | 1.0682 | 0.47152 | 0.25392 | 0.15479 | 0.10268 | 0.072401 | 0.053457 | 0.040913 | 0.032226 | 0.025987 | 0.021368 | 0.017862 | 0.015142 | 0.012993 | 0.011267 | 0.0098618 | 0.0087027 | 0.007736 | 0.0069218 | 0.0062299 | 0.005637 | 0.0051253 | 0.0046806 | 0.0042918 | 0.0039499 | 0.0036477 | 0.0033793 | 0.0031399 | 0.0029253 | 0.0027324 | 0.0025582 | 0.0024004 | 0.002257 | 0.0021264 | 0.002007 | 0.0018975 | 0.001797 | 0.0017044 | 0.001619 | 0.00154 | 0.0014667 | 0.0013987 | 0.0013355 | 0.0012765 | 0.0012215 | 0.00117 | 0.0011218 | 0.0010766 | 0.0010342 | 0.00099427 | 0.0009567 | 0.00092128 | 0.00088786 | 0.00085627 | 0.00082639 | 0.0007981 | 0.00077128 | 0.00074583 | 0.00072166 | 0.00069869 | 0.00067683 | 0.00065602 | 0.00063618 | 0.00061726 | 0.0005992 | 0.00058195 | 0.00056546 | 0.00054969 | 0.00053458 | 0.00052012 | 0.00050625 | 0.00049295 | 0.00048019 | 0.00046794 | 0.00045616 | 0.00044484 | 0.00043395 | 0.00042347 | 0.00041338 | 0.00040366 | 0.0003943 | 0.00038526 | 0.00037655 | 0.00036814 | 0.00036001 | 0.00035217 | 0.00034459 | 0.00033726 | 0.00033017 | 0.00032331 | 0.00031667 | 0.00031024 | 0.00030401 | 0.00029797 | 0.00029212 | 0.00028645 | 0.00028095 | 0.00027561 | 0.00027043 | 0.25392
650 | 33.1126 | 4.0667 | 1.2461 | 0.55176 | 0.29802 | 0.18218 | 0.12117 | 0.085641 | 0.063375 | 0.048605 | 0.038359 | 0.030987 | 0.025523 | 0.021368 | 0.018141 | 0.015587 | 0.013534 | 0.01186 | 0.010478 | 0.0093243 | 0.0083513 | 0.0075236 | 0.0068138 | 0.0062005 | 0.0056671 | 0.0052004 | 0.0047897 | 0.0044263 | 0.0041034 | 0.003815 | 0.0035565 | 0.0033239 | 0.0031137 | 0.0029232 | 0.0027501 | 0.0025922 | 0.0024478 | 0.0023153 | 0.0021936 | 0.0020815 | 0.001978 | 0.0018822 | 0.0017933 | 0.0017108 | 0.001634 | 0.0015624 | 0.0014955 | 0.001433 | 0.0013744 | 0.0013194 | 0.0012678 | 0.0012192 | 0.0011735 | 0.0011303 | 0.0010896 | 0.0010511 | 0.0010147 | 0.00098015 | 0.00094743 | 0.00091638 | 0.00088688 | 0.00085883 | 0.00083213 | 0.00080671 | 0.00078247 | 0.00075934 | 0.00073727 | 0.00071617 | 0.000696 | 0.0006767 | 0.00065822 | 0.00064052 | 0.00062354 | 0.00060726 | 0.00059163 | 0.00057662 | 0.00056219 | 0.00054832 | 0.00053497 | 0.00052213 | 0.00050976 | 0.00049784 | 0.00048635 | 0.00047526 | 0.00046457 | 0.00045425 | 0.00044428 | 0.00043465 | 0.00042534 | 0.00041634 | 0.00040763 | 0.00039921 | 0.00039105 | 0.00038315 | 0.0003755 | 0.00036808 | 0.00036089 | 0.00035392 | 0.00034715 | 0.00034059 | 0.00033421 | 0.29802
600 | 38.9076 | 4.7933 | 1.4739 | 0.65497 | 0.35495 | 0.21766 | 0.14518 | 0.10289 | 0.076325 | 0.058669 | 0.046398 | 0.037555 | 0.030987 | 0.025987 | 0.022096 | 0.019014 | 0.016532 | 0.014506 | 0.01283 | 0.01143 | 0.010249 | 0.0092421 | 0.0083781 | 0.0076309 | 0.0069804 | 0.0064107 | 0.0059089 | 0.0054647 | 0.0050695 | 0.0047164 | 0.0043996 | 0.0041143 | 0.0038564 | 0.0036225 | 0.0034097 | 0.0032156 | 0.0030379 | 0.002875 | 0.0027251 | 0.0025869 | 0.0024593 | 0.0023411 | 0.0022315 | 0.0021296 | 0.0020347 | 0.0019462 | 0.0018636 | 0.0017862 | 0.0017137 | 0.0016457 | 0.0015818 | 0.0015216 | 0.0014649 | 0.0014114 | 0.0013609 | 0.0013132 | 0.001268 | 0.0012252 | 0.0011846 | 0.001146 | 0.0011093 | 0.0010745 | 0.0010413 | 0.0010097 | 0.00097957 | 0.0009508 | 0.00092334 | 0.00089708 | 0.00087198 | 0.00084795 | 0.00082493 | 0.00080288 | 0.00078173 | 0.00076144 | 0.00074196 | 0.00072324 | 0.00070525 | 0.00068795 | 0.00067131 | 0.00065528 | 0.00063984 | 0.00062497 | 0.00061062 | 0.00059679 | 0.00058343 | 0.00057054 | 0.00055809 | 0.00054606 | 0.00053442 | 0.00052317 | 0.00051229 | 0.00050176 | 0.00049156 | 0.00048168 | 0.00047211 | 0.00046283 | 0.00045383 | 0.00044511 | 0.00043664 | 0.00042843 | 0.00042045 | 0.35495
550 | 46.4109 | 5.7402 | 1.7725 | 0.79086 | 0.43022 | 0.26474 | 0.17715 | 0.12591 | 0.093656 | 0.07217 | 0.057205 | 0.046398 | 0.038359 | 0.032226 | 0.027447 | 0.023655 | 0.020597 | 0.018097 | 0.016028 | 0.014296 | 0.012832 | 0.011584 | 0.010512 | 0.0095831 | 0.0087741 | 0.0080648 | 0.0074395 | 0.0068855 | 0.0063922 | 0.0059511 | 0.005555 | 0.005198 | 0.0048751 | 0.0045821 | 0.0043154 | 0.0040718 | 0.0038488 | 0.0036441 | 0.0034558 | 0.003282 | 0.0031214 | 0.0029727 | 0.0028346 | 0.0027063 | 0.0025867 | 0.0024751 | 0.0023708 | 0.0022731 | 0.0021816 | 0.0020957 | 0.0020149 | 0.0019388 | 0.0018671 | 0.0017995 | 0.0017356 | 0.0016751 | 0.0016179 | 0.0015636 | 0.0015121 | 0.0014633 | 0.0014168 | 0.0013726 | 0.0013305 | 0.0012904 | 0.0012521 | 0.0012156 | 0.0011807 | 0.0011473 | 0.0011154 | 0.0010849 | 0.0010556 | 0.0010276 | 0.0010007 | 0.00097488 | 0.00095009 | 0.00092627 | 0.00090337 | 0.00088134 | 0.00086014 | 0.00083972 | 0.00082005 | 0.0008011 | 0.00078282 | 0.00076518 | 0.00074815 | 0.00073172 | 0.00071583 | 0.00070048 | 0.00068564 | 0.00067129 | 0.0006574 | 0.00064395 | 0.00063093 | 0.00061832 | 0.0006061 | 0.00059425 | 0.00058276 | 0.00057161 | 0.00056079 | 0.00055029 | 0.0005401 | 0.43022
500 | 56.372 | 7.0071 | 2.1746 | 0.97484 | 0.5326 | 0.32904 | 0.22096 | 0.15757 | 0.11755 | 0.090825 | 0.07217 | 0.058669 | 0.048605 | 0.040913 | 0.034909 | 0.030136 | 0.026281 | 0.023124 | 0.020507 | 0.018314 | 0.016459 | 0.014874 | 0.013511 | 0.01233 | 0.0113 | 0.010396 | 0.0095977 | 0.00889 | 0.0082593 | 0.0076949 | 0.0071877 | 0.0067302 | 0.0063161 | 0.00594 | 0.0055974 | 0.0052844 | 0.0049976 | 0.0047342 | 0.0044917 | 0.0042679 | 0.0040609 | 0.003869 | 0.0036909 | 0.0035251 | 0.0033706 | 0.0032264 | 0.0030916 | 0.0029653 | 0.0028468 | 0.0027355 | 0.0026309 | 0.0025324 | 0.0024394 | 0.0023517 | 0.0022688 | 0.0021904 | 0.0021161 | 0.0020456 | 0.0019788 | 0.0019153 | 0.0018549 | 0.0017974 | 0.0017427 | 0.0016905 | 0.0016407 | 0.0015932 | 0.0015478 | 0.0015043 | 0.0014628 | 0.001423 | 0.0013848 | 0.0013483 | 0.0013132 | 0.0012796 | 0.0012472 | 0.0012161 | 0.0011863 | 0.0011575 | 0.0011298 | 0.0011032 | 0.0010775 | 0.0010527 | 0.0010288 | 0.0010058 | 0.00098355 | 0.00096206 | 0.0009413 | 0.00092123 | 0.00090182 | 0.00088304 | 0.00086487 | 0.00084728 | 0.00083024 | 0.00081373 | 0.00079773 | 0.00078221 | 0.00076717 | 0.00075257 | 0.0007384 | 0.00072464 | 0.00071129 | 0.5326
450 | 70.002 | 8.757 | 2.7342 | 1.2325 | 0.67675 | 0.41998 | 0.28317 | 0.20266 | 0.15168 | 0.11755 | 0.093656 | 0.076325 | 0.063375 | 0.053457 | 0.045699 | 0.039521 | 0.034522 | 0.030422 | 0.027018 | 0.024161 | 0.02174 | 0.019671 | 0.017888 | 0.016341 | 0.01499 | 0.013803 | 0.012755 | 0.011824 | 0.010994 | 0.01025 | 0.0095817 | 0.0089779 | 0.008431 | 0.0079338 | 0.0074806 | 0.0070663 | 0.0066864 | 0.0063373 | 0.0060157 | 0.0057186 | 0.0054438 | 0.0051889 | 0.004952 | 0.0047316 | 0.004526 | 0.004334 | 0.0041544 | 0.0039861 | 0.0038282 | 0.0036798 | 0.0035402 | 0.0034086 | 0.0032845 | 0.0031674 | 0.0030566 | 0.0029517 | 0.0028523 | 0.0027581 | 0.0026686 | 0.0025836 | 0.0025027 | 0.0024257 | 0.0023524 | 0.0022824 | 0.0022157 | 0.0021519 | 0.002091 | 0.0020327 | 0.0019769 | 0.0019235 | 0.0018723 | 0.0018232 | 0.0017761 | 0.0017309 | 0.0016874 | 0.0016456 | 0.0016054 | 0.0015668 | 0.0015295 | 0.0014937 | 0.0014591 | 0.0014258 | 0.0013936 | 0.0013626 | 0.0013326 | 0.0013037 | 0.0012757 | 0.0012486 | 0.0012225 | 0.0011972 | 0.0011727 | 0.0011489 | 0.001126 | 0.0011037 | 0.0010821 | 0.0010612 | 0.0010409 | 0.0010212 | 0.001002 | 0.00098348 | 0.00096544 | 0.67675
400 | 89.3624 | 11.2718 | 3.5458 | 1.6089 | 0.88859 | 0.55428 | 0.37543 | 0.26978 | 0.20266 | 0.15757 | 0.12591 | 0.10289 | 0.085641 | 0.072401 | 0.062022 | 0.053738 | 0.047024 | 0.041506 | 0.036918 | 0.033061 | 0.029787 | 0.026985 | 0.024568 | 0.022468 | 0.020631 | 0.019016 | 0.017588 | 0.016319 | 0.015186 | 0.014169 | 0.013255 | 0.012428 | 0.011679 | 0.010997 | 0.010375 | 0.0098064 | 0.0092844 | 0.0088044 | 0.0083618 | 0.0079528 | 0.0075741 | 0.0072227 | 0.0068961 | 0.0065918 | 0.006308 | 0.0060428 | 0.0057945 | 0.0055617 | 0.0053433 | 0.0051379 | 0.0049445 | 0.0047623 | 0.0045903 | 0.0044279 | 0.0042742 | 0.0041287 | 0.0039908 | 0.00386 | 0.0037357 | 0.0036176 | 0.0035052 | 0.0033981 | 0.0032961 | 0.0031988 | 0.0031059 | 0.0030172 | 0.0029323 | 0.0028512 | 0.0027735 | 0.002699 | 0.0026277 | 0.0025592 | 0.0024935 | 0.0024304 | 0.0023698 | 0.0023115 | 0.0022554 | 0.0022014 | 0.0021494 | 0.0020993 | 0.002051 | 0.0020045 | 0.0019595 | 0.0019161 | 0.0018742 | 0.0018338 | 0.0017946 | 0.0017568 | 0.0017202 | 0.0016848 | 0.0016505 | 0.0016173 | 0.0015851 | 0.001554 | 0.0015237 | 0.0014944 | 0.001466 | 0.0014384 | 0.0014116 | 0.0013855 | 0.0013603 | 0.88859
350 | 118.1945 | 15.0722 | 4.7857 | 2.189 | 1.2173 | 0.76384 | 0.52006 | 0.37543 | 0.28317 | 0.22096 | 0.17715 | 0.14518 | 0.12117 | 0.10268 | 0.088156 | 0.076538 | 0.0671 | 0.059329 | 0.052855 | 0.047403 | 0.042768 | 0.038795 | 0.035363 | 0.032377 | 0.029762 | 0.02746 | 0.025422 | 0.023608 | 0.021987 | 0.020532 | 0.019222 | 0.018036 | 0.01696 | 0.015981 | 0.015087 | 0.014268 | 0.013516 | 0.012824 | 0.012186 | 0.011596 | 0.011049 | 0.010541 | 0.010069 | 0.0096286 | 0.0092178 | 0.0088337 | 0.008474 | 0.0081366 | 0.0078197 | 0.0075217 | 0.007241 | 0.0069764 | 0.0067265 | 0.0064904 | 0.006267 | 0.0060553 | 0.0058547 | 0.0056642 | 0.0054832 | 0.0053112 | 0.0051474 | 0.0049914 | 0.0048426 | 0.0047007 | 0.0045652 | 0.0044357 | 0.0043118 | 0.0041933 | 0.0040798 | 0.0039711 | 0.0038668 | 0.0037667 | 0.0036706 | 0.0035784 | 0.0034897 | 0.0034044 | 0.0033223 | 0.0032433 | 0.0031671 | 0.0030938 | 0.0030231 | 0.0029548 | 0.002889 | 0.0028254 | 0.002764 | 0.0027047 | 0.0026473 | 0.0025918 | 0.0025381 | 0.0024862 | 0.0024358 | 0.0023871 | 0.0023399 | 0.0022941 | 0.0022497 | 0.0022067 | 0.0021649 | 0.0021244 | 0.002085 | 0.0020467 | 0.0020096 | 1.2173
300 | 163.8716 | 21.2064 | 6.8142 | 3.1476 | 1.7648 | 1.1152 | 0.76384 | 0.55428 | 0.41998 | 0.32904 | 0.26474 | 0.21766 | 0.18218 | 0.15479 | 0.13321 | 0.11591 | 0.10182 | 0.090189 | 0.080483 | 0.072294 | 0.06532 | 0.059332 | 0.054151 | 0.049636 | 0.045679 | 0.042189 | 0.039095 | 0.03634 | 0.033874 | 0.031659 | 0.02966 | 0.027852 | 0.026209 | 0.024712 | 0.023344 | 0.02209 | 0.020938 | 0.019877 | 0.018898 | 0.017992 | 0.017151 | 0.016371 | 0.015644 | 0.014967 | 0.014334 | 0.013742 | 0.013188 | 0.012667 | 0.012178 | 0.011718 | 0.011285 | 0.010876 | 0.01049 | 0.010124 | 0.0097786 | 0.009451 | 0.0091403 | 0.0088452 | 0.0085648 | 0.0082981 | 0.0080441 | 0.0078021 | 0.0075713 | 0.007351 | 0.0071406 | 0.0069395 | 0.0067471 | 0.006563 | 0.0063865 | 0.0062175 | 0.0060553 | 0.0058996 | 0.0057501 | 0.0056065 | 0.0054685 | 0.0053356 | 0.0052078 | 0.0050847 | 0.0049661 | 0.0048518 | 0.0047415 | 0.0046352 | 0.0045325 | 0.0044333 | 0.0043376 | 0.004245 | 0.0041554 | 0.0040688 | 0.003985 | 0.0039039 | 0.0038254 | 0.0037492 | 0.0036755 | 0.003604 | 0.0035346 | 0.0034673 | 0.003402 | 0.0033386 | 0.0032771 | 0.0032173 | 0.0031592 | 1.7648
250 | 242.5952 | 32.0402 | 10.4576 | 4.8906 | 2.7697 | 1.7648 | 1.2173 | 0.88859 | 0.67675 | 0.5326 | 0.43022 | 0.35495 | 0.29802 | 0.25392 | 0.21907 | 0.19105 | 0.16817 | 0.14926 | 0.13343 | 0.12004 | 0.10863 | 0.098806 | 0.090294 | 0.082867 | 0.076345 | 0.070587 | 0.065476 | 0.060918 | 0.056834 | 0.053161 | 0.049845 | 0.04684 | 0.044108 | 0.041616 | 0.039337 | 0.037247 | 0.035325 | 0.033554 | 0.031917 | 0.030402 | 0.028996 | 0.027689 | 0.026472 | 0.025337 | 0.024275 | 0.023282 | 0.022351 | 0.021477 | 0.020655 | 0.019881 | 0.019152 | 0.018464 | 0.017813 | 0.017198 | 0.016615 | 0.016063 | 0.015539 | 0.015041 | 0.014568 | 0.014118 | 0.013689 | 0.01328 | 0.01289 | 0.012518 | 0.012162 | 0.011822 | 0.011496 | 0.011185 | 0.010886 | 0.0106 | 0.010325 | 0.010061 | 0.0098082 | 0.0095648 | 0.0093307 | 0.0091055 | 0.0088887 | 0.0086798 | 0.0084786 | 0.0082846 | 0.0080975 | 0.0079169 | 0.0077425 | 0.0075741 | 0.0074114 | 0.0072541 | 0.007102 | 0.0069548 | 0.0068123 | 0.0066744 | 0.0065408 | 0.0064114 | 0.0062859 | 0.0061642 | 0.0060462 | 0.0059317 | 0.0058206 | 0.0057127 | 0.0056079 | 0.0055061 | 0.0054071 | 2.7697
200 | 395.8077 | 53.832 | 17.9464 | 8.5282 | 4.8906 | 3.1476 | 2.189 | 1.6089 | 1.2325 | 0.97484 | 0.79086 | 0.65497 | 0.55176 | 0.47152 | 0.40789 | 0.35657 | 0.31456 | 0.27972 | 0.25051 | 0.22575 | 0.20459 | 0.18636 | 0.17052 | 0.15668 | 0.14452 | 0.13376 | 0.12419 | 0.11565 | 0.10799 | 0.1011 | 0.094861 | 0.089207 | 0.084061 | 0.079364 | 0.075064 | 0.071117 | 0.067485 | 0.064135 | 0.061037 | 0.058167 | 0.055503 | 0.053025 | 0.050715 | 0.048559 | 0.046544 | 0.044656 | 0.042885 | 0.041222 | 0.039657 | 0.038184 | 0.036794 | 0.035482 | 0.034242 | 0.033069 | 0.031957 | 0.030903 | 0.029902 | 0.028951 | 0.028047 | 0.027186 | 0.026366 | 0.025584 | 0.024838 | 0.024125 | 0.023444 | 0.022793 | 0.022169 | 0.021572 | 0.021 | 0.020451 | 0.019924 | 0.019418 | 0.018932 | 0.018465 | 0.018016 | 0.017584 | 0.017168 | 0.016767 | 0.01638 | 0.016007 | 0.015648 | 0.015301 | 0.014965 | 0.014642 | 0.014329 | 0.014026 | 0.013734 | 0.01345 | 0.013176 | 0.012911 | 0.012654 | 0.012405 | 0.012163 | 0.011929 | 0.011701 | 0.011481 | 0.011267 | 0.011059 | 0.010857 | 0.010661 | 0.01047 | 4.8906
150 | 756.6763 | 107.6077 | 36.9658 | 17.9464 | 10.4576 | 6.8142 | 4.7857 | 3.5458 | 2.7342 | 2.1746 | 1.7725 | 1.4739 | 1.2461 | 1.0682 | 0.92653 | 0.81192 | 0.71782 | 0.63957 | 0.57378 | 0.51792 | 0.47006 | 0.42874 | 0.39279 | 0.36133 | 0.33362 | 0.30908 | 0.28724 | 0.26771 | 0.25018 | 0.23438 | 0.22008 | 0.20709 | 0.19527 | 0.18446 | 0.17456 | 0.16547 | 0.1571 | 0.14937 | 0.14222 | 0.13559 | 0.12943 | 0.1237 | 0.11835 | 0.11336 | 0.10869 | 0.10432 | 0.10021 | 0.096352 | 0.092721 | 0.089301 | 0.086074 | 0.083026 | 0.080143 | 0.077415 | 0.074829 | 0.072376 | 0.070047 | 0.067833 | 0.065727 | 0.063722 | 0.061811 | 0.059988 | 0.058249 | 0.056587 | 0.054998 | 0.053478 | 0.052023 | 0.050629 | 0.049293 | 0.048011 | 0.046781 | 0.0456 | 0.044464 | 0.043373 | 0.042323 | 0.041312 | 0.040339 | 0.039401 | 0.038497 | 0.037625 | 0.036783 | 0.035971 | 0.035187 | 0.034429 | 0.033696 | 0.032988 | 0.032302 | 0.031639 | 0.030997 | 0.030375 | 0.029773 | 0.029189 | 0.028622 | 0.028073 | 0.02754 | 0.027023 | 0.026521 | 0.026034 | 0.02556 | 0.0251 | 0.024653 | 10.4576
100 | 1956.2757 | 299.4654 | 107.6077 | 53.832 | 32.0402 | 21.2064 | 15.0722 | 11.2718 | 8.757 | 7.0071 | 5.7402 | 4.7933 | 4.0667 | 3.4966 | 3.041 | 2.6709 | 2.366 | 2.1118 | 1.8975 | 1.7151 | 1.5586 | 1.4231 | 1.3051 | 1.2017 | 1.1104 | 1.0295 | 0.95744 | 0.89292 | 0.83493 | 0.7826 | 0.73521 | 0.69216 | 0.65291 | 0.61703 | 0.58413 | 0.55389 | 0.52603 | 0.5003 | 0.47648 | 0.45439 | 0.43386 | 0.41475 | 0.39692 | 0.38026 | 0.36466 | 0.35005 | 0.33633 | 0.32344 | 0.3113 | 0.29986 | 0.28907 | 0.27887 | 0.26922 | 0.26009 | 0.25143 | 0.24322 | 0.23542 | 0.228 | 0.22095 | 0.21423 | 0.20782 | 0.20171 | 0.19588 | 0.1903 | 0.18498 | 0.17988 | 0.175 | 0.17032 | 0.16584 | 0.16153 | 0.15741 | 0.15344 | 0.14963 | 0.14596 | 0.14244 | 0.13904 | 0.13577 | 0.13262 | 0.12959 | 0.12666 | 0.12383 | 0.1211 | 0.11847 | 0.11592 | 0.11346 | 0.11108 | 0.10877 | 0.10654 | 0.10438 | 0.10229 | 0.10027 | 0.098305 | 0.096401 | 0.094554 | 0.092762 | 0.091024 | 0.089335 | 0.087696 | 0.086103 | 0.084555 | 0.08305 | 32.0402
50 | 11115.6928 | 1956.2757 | 756.6763 | 395.8077 | 242.5952 | 163.8716 | 118.1945 | 89.3624 | 70.002 | 56.372 | 46.4109 | 38.9076 | 33.1126 | 28.5422 | 24.8725 | 21.8804 | 19.4078 | 17.3403 | 15.5934 | 14.1037 | 12.8226 | 11.7127 | 10.7445 | 9.8946 | 9.1444 | 8.4787 | 7.8851 | 7.3535 | 6.8755 | 6.444 | 6.0531 | 5.6978 | 5.3738 | 5.0776 | 4.806 | 4.5564 | 4.3263 | 4.1138 | 3.9171 | 3.7347 | 3.5651 | 3.4073 | 3.26 | 3.1225 | 2.9938 | 2.8731 | 2.7599 | 2.6535 | 2.5533 | 2.4589 | 2.3699 | 2.2858 | 2.2062 | 2.1309 | 2.0595 | 1.9918 | 1.9275 | 1.8664 | 1.8083 | 1.7529 | 1.7002 | 1.6499 | 1.6018 | 1.556 | 1.5121 | 1.4701 | 1.43 | 1.3915 | 1.3546 | 1.3193 | 1.2853 | 1.2527 | 1.2214 | 1.1913 | 1.1623 | 1.1344 | 1.1076 | 1.0817 | 1.0568 | 1.0327 | 1.0095 | 0.98711 | 0.96548 | 0.94458 | 0.92439 | 0.90486 | 0.88597 | 0.86769 | 0.85 | 0.83286 | 0.81626 | 0.80017 | 0.78457 | 0.76945 | 0.75477 | 0.74053 | 0.72671 | 0.71328 | 0.70024 | 0.68757 | 0.67526 | 242.5952
[101 empty] | Duct Size | 385.4856

## Material (hidden)
Duct Material | Absolute Roughness (inches) | Absolute Roughness (mm) | Duct Loss Setting
Galvanised Iron | 0.006 | 0.15 | Exact Value | 250 x 386 mm Duct Size
Drawn Brass | 6e-05 | 0.0015 | Rounded Value | 250 x 400 mm Duct Size
Drawn Copper | 6e-05 | 0.0015
Commercial Steel | 0.0018 | 0.045
Wrought Iron | 0.0018 | 0.045
Asphalted Cast Iron | 0.0048 | 0.12
Cast Iron | 0.102 | 2.55
Wood Stave | 0.072-0.036 | 0.9
Concrete | 0.012-0.12 | 3
Riveted Steel | 0.036-0.36 | 9